## Introduction
Introduction
Why undertake regular maintenance and monitoring?
Maintenance and monitoring of the water supply system is the way we ensure that water supplies are safe to drink. Regular scheduled maintenance will ensure that: - the key components of the system are working as intended - the risk of contamination is kept low - any contaminants accumulating in the system are removed. Monitoring is a regular check that the water is safe to drink but it only tells us when water is unsafe to drink.
Purpose of the checklist tool and how to use it
The checklist tool provide simple maintenance and servicing guidelines for each supply category.
To select or deselect multiple options in a list, click on multi-select button until it is coloured:
To clear a filter, click on the clear filter button:
1. Select the water source and supply size
Select the water source/sources and size of supply, for example roof and bore supply for a school supplying 200 people: This will show the supply category: Medium - Rules (no need to select this)
To deselect or clear the filter, press: To select mulitple options, right click on the slicer and select:
If the supply serves less than 100 people and 3 or fewer buildings, with multiple water sources, please select the sources separately as there will be a different set of rules applied to each source, for example a school supplying 80 people and 2 buildings with roof and bore water: This will show the supply category as: (no need to select this)
To deselect or clear the filter, press: To select mulitple options, right click on the slicer and select:
2. Check the equipment / systems relevant to the supply
Deselect equipment not relevant to the water supply, for example, no media filter or membrane filter. To deselect equipment, right click on the slicer and select:
Purpose of the data capture tool and how to use it
1. Select the relevant data capture sheet
A 'Data Capture' sheet is available for each supply size. This should be used for recording when scheduled tasks have been completed and for capturing monitoring data.
There are Data Capture sheets for different supply sizes, only use the one relevant to the school supply size. For example supplying 80 people with drinking water, use this sheet:
2. Select equipment / systems relevant to supply
Deselect equipment / systems that are not relevant to the school: For example, a bore supply (no roof or surface catchment) with media filtration, Cartridge filtration, UV and water tanks:
An example on how to fill the data sheet is provided in the first column of the data sheet:
3. Fill the sheet every time maintenance or monitoring is done
Monitoring requirements that the school is not currently undertaking may be hidden by right-clicking on the row in the relevant data capture sheet and choosing hide.

## Maintenance Checklists
Supply size | Source | Supply Category | Reference | Area | Equipment / System | Activity | Frequency | Data to capture
≤100 people & > 3 buildings | Groundwater | Small - Rules | D1.2 | Distribution | Backflow | Assess the distribution system for backflow risk. | Annually
≤100 people & > 3 buildings | Surface water | Small - Rules | D1.2 | Distribution | Backflow | Assess the distribution system for backflow risk. | Annually
≤100 people & > 3 buildings | Roof | Small - Rules | D1.2 | Distribution | Backflow | Assess the distribution system for backflow risk. | Annually
≤100 people & > 3 buildings | Roof & Groundwater | Small - Rules | D1.2 | Distribution | Backflow | Assess the distribution system for backflow risk. | Annually
≤100 people & > 3 buildings | Roof & Surface water | Small - Rules | D1.2 | Distribution | Backflow | Assess the distribution system for backflow risk. | Annually
≤100 people & > 3 buildings | Surface & Groundwater | Small - Rules | D1.2 | Distribution | Backflow | Assess the distribution system for backflow risk. | Annually
≤100 people & > 3 buildings | Roof, Surface & Groundwater | Small - Rules | D1.2 | Distribution | Backflow | Assess the distribution system for backflow risk. | Annually
<100 people & ≤3 buildings | Roof | Acceptable Solution - Roof |  | Distribution | Backflow | Assess the distribution system for backflow risk. | Annually
<100 people & ≤3 buildings | Groundwater | Acceptable Solution - Spring & Bore |  | Distribution | Backflow | Assess the distribution system for backflow risk. | Annually
101 - 500 people | Surface water | Medium - Rules | D2.7 | Distribution | Backflow | Assess the distribution system for backflow risk. | Annually
101 - 500 people | Roof & Groundwater | Medium - Rules | D2.7 | Distribution | Backflow | Assess the distribution system for backflow risk. | Annually
101 - 500 people | Surface & Groundwater | Medium - Rules | D2.7 | Distribution | Backflow | Assess the distribution system for backflow risk. | Annually
101 - 500 people | Groundwater | Medium - Rules | D2.7 | Distribution | Backflow | Assess the distribution system for backflow risk. | Annually
101 - 500 people | Roof | Medium - Rules | D2.7 | Distribution | Backflow | Assess the distribution system for backflow risk. | Annually
101 - 500 people | Roof & Surface water | Medium - Rules | D2.7 | Distribution | Backflow | Assess the distribution system for backflow risk. | Annually
101 - 500 people | Roof, Surface & Groundwater | Medium - Rules | D2.7 | Distribution | Backflow | Assess the distribution system for backflow risk. | Annually
>500 people | Surface water | Large - Rules |  | Treatment | Media filter | Check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
>500 people | Roof | Large - Rules |  | Treatment | Media filter | Check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
>500 people | Roof & Groundwater | Large - Rules |  | Treatment | Media filter | Check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
>500 people | Roof & Surface water | Large - Rules |  | Treatment | Media filter | Check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
>500 people | Surface & Groundwater | Large - Rules |  | Treatment | Media filter | Check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
>500 people | Roof, Surface & Groundwater | Large - Rules |  | Treatment | Media filter | Check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
>500 people | Groundwater | Large - Rules |  | Treatment | Media filter | Check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
≤100 people & > 3 buildings | Surface water | Small - Rules | T1.1 | Treatment | Media filter | Check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
≤100 people & > 3 buildings | Roof | Small - Rules |  | Treatment | Media filter | Check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
≤100 people & > 3 buildings | Roof & Groundwater | Small - Rules |  | Treatment | Media filter | Check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
≤100 people & > 3 buildings | Roof & Surface water | Small - Rules | T1.1 | Treatment | Media filter | Check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
≤100 people & > 3 buildings | Surface & Groundwater | Small - Rules | T1.1 | Treatment | Media filter | Check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
≤100 people & > 3 buildings | Roof, Surface & Groundwater | Small - Rules | T1.1 | Treatment | Media filter | Check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
≤100 people & > 3 buildings | Groundwater | Small - Rules |  | Treatment | Media filter | Check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
101 - 500 people | Surface water | Medium - Rules | T2.3 | Treatment | Media filter | Check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
101 - 500 people | Roof | Medium - Rules | T2.3 | Treatment | Media filter | Check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
101 - 500 people | Roof & Groundwater | Medium - Rules | T2.3 | Treatment | Media filter | Check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
101 - 500 people | Roof & Surface water | Medium - Rules | T2.3 | Treatment | Media filter | Check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
101 - 500 people | Surface & Groundwater | Medium - Rules | T2.3 | Treatment | Media filter | Check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
101 - 500 people | Roof, Surface & Groundwater | Medium - Rules | T2.3 | Treatment | Media filter | Check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
101 - 500 people | Groundwater | Medium - Rules | T2.3 | Treatment | Media filter | Check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
>500 people | Surface water | Large - Rules | T3.73 - T3.79 | Treatment | Membrane filter | Check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
>500 people | Roof | Large - Rules | T3.73 - T3.80 | Treatment | Membrane filter | Check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
>500 people | Roof & Groundwater | Large - Rules | T3.73 - T3.80 | Treatment | Membrane filter | Check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
>500 people | Roof & Surface water | Large - Rules | T3.73 - T3.80 | Treatment | Membrane filter | Check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
>500 people | Surface & Groundwater | Large - Rules | T3.73 - T3.80 | Treatment | Membrane filter | Check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
>500 people | Roof, Surface & Groundwater | Large - Rules | T3.73 - T3.80 | Treatment | Membrane filter | Check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
>500 people | Groundwater | Large - Rules | T3.73 - T3.79 | Treatment | Membrane filter | Check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
101 - 500 people | Surface water | Medium - Rules | T2.3 | Treatment | Membrane filter | Check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
101 - 500 people | Roof | Medium - Rules | T2.3 | Treatment | Membrane filter | Check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
101 - 500 people | Roof & Groundwater | Medium - Rules | T2.3 | Treatment | Membrane filter | Check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
101 - 500 people | Roof & Surface water | Medium - Rules | T2.3 | Treatment | Membrane filter | Check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
101 - 500 people | Surface & Groundwater | Medium - Rules | T2.3 | Treatment | Membrane filter | Check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
101 - 500 people | Roof, Surface & Groundwater | Medium - Rules | T2.3 | Treatment | Membrane filter | Check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
101 - 500 people | Groundwater | Medium - Rules | T2.3 | Treatment | Membrane filter | Check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
<100 people & ≤3 buildings | Groundwater | Acceptable Solution - Spring & Bore | 2.3 | Treatment | Pre-treatment, e.g. iron and manganese removal, back-washable filters, aeration | Check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
>500 people | Roof | Large - Rules |  | Source - Roof | Supply pump | Check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
>500 people | Surface water | Large - Rules |  | Source - Surface | Supply pump | Check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
≤100 people & > 3 buildings | Roof | Small - Rules |  | Source - Roof | Supply pump | Check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
>500 people | Roof & Groundwater | Large - Rules |  | Source - Roof | Supply pump | Check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
>500 people | Roof & Surface water | Large - Rules |  | Source - Roof & Surface | Supply pump | Check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
>500 people | Surface & Groundwater | Large - Rules |  | Source - Bore | Supply pump | Check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
>500 people | Roof, Surface & Groundwater | Large - Rules |  | Source - Roof & Surface | Supply pump | Check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
≤100 people & > 3 buildings | Surface water | Small - Rules |  | Source - Surface | Supply pump | Check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
101 - 500 people | Roof | Medium - Rules |  | Source - Roof | Supply pump | Check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
≤100 people & > 3 buildings | Roof & Groundwater | Small - Rules |  | Source - Roof | Supply pump | Check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
≤100 people & > 3 buildings | Roof & Surface water | Small - Rules |  | Source - Roof & Surface | Supply pump | Check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
≤100 people & > 3 buildings | Surface & Groundwater | Small - Rules |  | Source - Surface | Supply pump | Check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
≤100 people & > 3 buildings | Roof, Surface & Groundwater | Small - Rules |  | Source - Roof & Surface | Supply pump | Check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
101 - 500 people | Surface water | Medium - Rules |  | Source - Surface | Supply pump | Check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
<100 people & ≤3 buildings | Roof | Acceptable Solution - Roof |  | Source - Roof | Supply pump | Check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
101 - 500 people | Roof & Groundwater | Medium - Rules |  | Source - Roof | Supply pump | Check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
101 - 500 people | Roof & Surface water | Medium - Rules |  | Source - Roof & Surface | Supply pump | Check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
101 - 500 people | Surface & Groundwater | Medium - Rules |  | Source - Surface | Supply pump | Check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
101 - 500 people | Roof, Surface & Groundwater | Medium - Rules |  | Source - Roof & Surface | Supply pump | Check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
<100 people & ≤3 buildings | Roof | Acceptable Solution - Roof |  | Source - Roof | First flush diverter | Clean first flush diverters. | Monthly
>500 people | Roof | Large - Rules |  | Source - Roof | First flush diverter | Check and remove any debris. | Monthly
>500 people | Roof & Groundwater | Large - Rules |  | Source - Roof | First flush diverter | Check and remove any debris. | Monthly
>500 people | Roof & Surface water | Large - Rules |  | Source - Roof | First flush diverter | Check and remove any debris. | Monthly
>500 people | Roof, Surface & Groundwater | Large - Rules |  | Source - Roof | First flush diverter | Check and remove any debris. | Monthly
>500 people | Roof | Large - Rules |  | Source - Roof | First flush diverter | Clean first flush diverters. | Monthly
101 - 500 people | Roof | Medium - Rules |  | Source - Roof | First flush diverter | Clean first flush diverters. | Monthly
101 - 500 people | Roof & Groundwater | Medium - Rules |  | Source - Roof | First flush diverter | Clean first flush diverters. | Monthly
101 - 500 people | Roof & Surface water | Medium - Rules |  | Source - Roof | First flush diverter | Clean first flush diverters. | Monthly
101 - 500 people | Roof, Surface & Groundwater | Medium - Rules |  | Source - Roof | First flush diverter | Clean first flush diverters. | Monthly
≤100 people & > 3 buildings | Roof | Small - Rules |  | Source - Roof | First flush diverter | Clean first flush diverters. | Monthly
≤100 people & > 3 buildings | Roof & Groundwater | Small - Rules |  | Source - Roof | First flush diverter | Clean first flush diverters. | Monthly
≤100 people & > 3 buildings | Roof & Surface water | Small - Rules |  | Source - Roof | First flush diverter | Clean first flush diverters. | Monthly
≤100 people & > 3 buildings | Roof, Surface & Groundwater | Small - Rules |  | Source - Roof | First flush diverter | Clean first flush diverters. | Monthly
<100 people & ≤3 buildings | Roof | Acceptable Solution - Roof | 3.d | Source - Roof | Guttering | Check and remove any debris. | Monthly
>500 people | Roof | Large - Rules |  | Source - Roof | Guttering | Check and remove any debris. | Monthly
>500 people | Roof & Groundwater | Large - Rules |  | Source - Roof | Guttering | Check and remove any debris. | Monthly
≤100 people & > 3 buildings | Surface water | Small - Rules | T1.1 | Storage - Surface water | Raw water tank | Check calmed bottom inlet and floating out take. | Annually
≤100 people & > 3 buildings | Roof & Surface water | Small - Rules | T1.1 | Storage - Surface water | Raw water tank | Check calmed bottom inlet and floating out take. | Annually
≤100 people & > 3 buildings | Surface & Groundwater | Small - Rules | T1.1 | Storage - Surface water | Raw water tank | Check calmed bottom inlet and floating out take. | Annually
≤100 people & > 3 buildings | Roof, Surface & Groundwater | Small - Rules | T1.1 | Storage - Surface water | Raw water tank | Check calmed bottom inlet and floating out take. | Annually
>500 people | Roof | Large - Rules | T3.70 | Treatment | Chlorination | Check chemical stock levels and re-stock if required. Maintain as per manufacturer's requirements. | Monthly
<100 people & ≤3 buildings | Groundwater | Acceptable Solution - Spring & Bore |  | Treatment | Water softener | Check chemical stock levels and re-stock if required. Maintain as per manufacturer's requirements. | Manufacturer’s requirements
>500 people | Surface water | Large - Rules | T3.69 | Treatment | Chlorination | Check chemical stock levels and re-stock if required. Maintain as per manufacturer's requirements. | Monthly
101 - 500 people | Roof | Medium - Rules | T2.7 | Treatment | Chlorination | Check chemical stock levels and re-stock if required. Maintain as per manufacturer's requirements. | Monthly
>500 people | Roof & Groundwater | Large - Rules | T3.70 | Treatment | Chlorination | Check chemical stock levels and re-stock if required. Maintain as per manufacturer's requirements. | Monthly
>500 people | Roof & Surface water | Large - Rules | T3.70 | Treatment | Chlorination | Check chemical stock levels and re-stock if required. Maintain as per manufacturer's requirements. | Monthly
>500 people | Surface & Groundwater | Large - Rules | T3.70 | Treatment | Chlorination | Check chemical stock levels and re-stock if required. Maintain as per manufacturer's requirements. | Monthly
>500 people | Roof, Surface & Groundwater | Large - Rules | T3.70 | Treatment | Chlorination | Check chemical stock levels and re-stock if required. Maintain as per manufacturer's requirements. | Monthly
101 - 500 people | Surface water | Medium - Rules | T2.7 | Treatment | Chlorination | Check chemical stock levels and re-stock if required. Maintain as per manufacturer's requirements. | Monthly
<100 people & ≤3 buildings | Roof | Acceptable Solution - Roof |  | Treatment | Water softener | Check chemical stock levels and re-stock if required. Maintain as per manufacturer's requirements. | Manufacturer’s requirements
101 - 500 people | Roof & Groundwater | Medium - Rules | T2.7 | Treatment | Chlorination | Check chemical stock levels and re-stock if required. Maintain as per manufacturer's requirements. | Monthly
101 - 500 people | Roof & Surface water | Medium - Rules | T2.7 | Treatment | Chlorination | Check chemical stock levels and re-stock if required. Maintain as per manufacturer's requirements. | Monthly
101 - 500 people | Surface & Groundwater | Medium - Rules | T2.7 | Treatment | Chlorination | Check chemical stock levels and re-stock if required. Maintain as per manufacturer's requirements. | Monthly
101 - 500 people | Roof, Surface & Groundwater | Medium - Rules | T2.7 | Treatment | Chlorination | Check chemical stock levels and re-stock if required. Maintain as per manufacturer's requirements. | Monthly
101 - 500 people | Groundwater | Medium - Rules | T2.7 | Treatment | Chlorination | Check chemical stock levels and re-stock if required. Maintain as per manufacturer's requirements. | Monthly
>500 people | Groundwater | Large - Rules | T3.69 | Treatment | Chlorination | Check chemical stock levels and re-stock if required. Maintain as per manufacturer's requirements. | Monthly
>500 people | Surface water | Large - Rules | T3.69 | Treatment | Cartridge filter | Check differential pressure across cartridge filters. Replace as per manufacturer's recommendations or if pressure and water quality indicate necessary. | Monthly
>500 people | Roof | Large - Rules | T3.70 | Treatment | Cartridge filter | Check differential pressure across cartridge filters. Replace as per manufacturer's recommendations or if pressure and water quality indicate necessary. | Monthly
>500 people | Roof & Groundwater | Large - Rules | T3.70 | Treatment | Cartridge filter | Check differential pressure across cartridge filters. Replace as per manufacturer's recommendations or if pressure and water quality indicate necessary. | Monthly
>500 people | Roof & Surface water | Large - Rules | T3.70 | Treatment | Cartridge filter | Check differential pressure across cartridge filters. Replace as per manufacturer's recommendations or if pressure and water quality indicate necessary. | Monthly
>500 people | Surface & Groundwater | Large - Rules | T3.70 | Treatment | Cartridge filter | Check differential pressure across cartridge filters. Replace as per manufacturer's recommendations or if pressure and water quality indicate necessary. | Monthly
>500 people | Roof, Surface & Groundwater | Large - Rules | T3.70 | Treatment | Cartridge filter | Check differential pressure across cartridge filters. Replace as per manufacturer's recommendations or if pressure and water quality indicate necessary. | Monthly
101 - 500 people | Surface water | Medium - Rules | T2.7 | Treatment | Cartridge filter | Check differential pressure across cartridge filters. Replace as per manufacturer's recommendations or if pressure and water quality indicate necessary. | Monthly
101 - 500 people | Roof | Medium - Rules | T2.7 | Treatment | Cartridge filter | Check differential pressure across cartridge filters. Replace as per manufacturer's recommendations or if pressure and water quality indicate necessary. | Monthly
101 - 500 people | Roof & Groundwater | Medium - Rules | T2.7 | Treatment | Cartridge filter | Check differential pressure across cartridge filters. Replace as per manufacturer's recommendations or if pressure and water quality indicate necessary. | Monthly
101 - 500 people | Roof & Surface water | Medium - Rules | T2.7 | Treatment | Cartridge filter | Check differential pressure across cartridge filters. Replace as per manufacturer's recommendations or if pressure and water quality indicate necessary. | Monthly
101 - 500 people | Surface & Groundwater | Medium - Rules | T2.7 | Treatment | Cartridge filter | Check differential pressure across cartridge filters. Replace as per manufacturer's recommendations or if pressure and water quality indicate necessary. | Monthly
101 - 500 people | Roof, Surface & Groundwater | Medium - Rules | T2.7 | Treatment | Cartridge filter | Check differential pressure across cartridge filters. Replace as per manufacturer's recommendations or if pressure and water quality indicate necessary. | Monthly
101 - 500 people | Groundwater | Medium - Rules | T2.7 | Treatment | Cartridge filter | Check differential pressure across cartridge filters. Replace as per manufacturer's recommendations or if pressure and water quality indicate necessary. | Monthly
>500 people | Groundwater | Large - Rules | T3.69 | Treatment | Cartridge filter | Check differential pressure across cartridge filters. Replace as per manufacturer's recommendations or if pressure and water quality indicate this is necessary. | Monthly
<100 people & ≤3 buildings | Groundwater | Acceptable Solution - Spring & Bore |  | Source - Bore | Bore | Check fencing excludes animals and bore head excludes stormwater. Repair any defects. | Monthly
≤100 people & > 3 buildings | Roof & Groundwater | Small - Rules |  | Source - Bore | Bore | Check fencing excludes animals and bore head excludes stormwater. Repair any defects. | Monthly
≤100 people & > 3 buildings | Surface & Groundwater | Small - Rules |  | Source - Bore | Bore | Check fencing excludes animals and bore head excludes stormwater. Repair any defects. | Monthly
≤100 people & > 3 buildings | Roof, Surface & Groundwater | Small - Rules |  | Source - Bore | Bore | Check fencing excludes animals and bore head excludes stormwater. Repair any defects. | Monthly
≤100 people & > 3 buildings | Groundwater | Small - Rules |  | Source - Bore | Bore | Check fencing excludes animals and bore head excludes stormwater. Repair any defects. | Monthly
101 - 500 people | Roof & Groundwater | Medium - Rules |  | Source - Bore | Bore | Check fencing excludes animals and bore head excludes stormwater. Repair any defects. | Monthly
101 - 500 people | Surface & Groundwater | Medium - Rules |  | Source - Bore | Bore | Check fencing excludes animals and bore head excludes stormwater. Repair any defects. | Monthly
101 - 500 people | Roof, Surface & Groundwater | Medium - Rules |  | Source - Bore | Bore | Check fencing excludes animals and bore head excludes stormwater. Repair any defects. | Monthly
101 - 500 people | Groundwater | Medium - Rules |  | Source - Bore | Bore | Check fencing excludes animals and bore head excludes stormwater. Repair any defects. | Monthly
≤100 people & > 3 buildings | Roof | Small - Rules |  | Storage | Tanks | Check lids are secure. Check tank openings (inlets, overflows, gaps) are all closed or screened to prevent access by vermin, birds and other sources of contamination. | 3 Monthly
≤100 people & > 3 buildings | Surface water | Small - Rules |  | Storage | Tanks | Check lids are secure. Check tank openings (inlets, overflows, gaps) are all closed or screened to prevent access by vermin, birds and other sources of contamination. | 3 Monthly
101 - 500 people | Roof | Medium - Rules |  | Storage | Tanks | Check lids are secure. Check tank openings (inlets, overflows, gaps) are all closed or screened to prevent access by vermin, birds and other sources of contamination. | 3 Monthly
≤100 people & > 3 buildings | Roof & Groundwater | Small - Rules |  | Storage | Tanks | Check lids are secure. Check tank openings (inlets, overflows, gaps) are all closed or screened to prevent access by vermin, birds and other sources of contamination. | 3 Monthly
≤100 people & > 3 buildings | Roof & Surface water | Small - Rules |  | Storage | Tanks | Check lids are secure. Check tank openings (inlets, overflows, gaps) are all closed or screened to prevent access by vermin, birds and other sources of contamination. | 3 Monthly
≤100 people & > 3 buildings | Surface & Groundwater | Small - Rules |  | Storage | Tanks | Check lids are secure. Check tank openings (inlets, overflows, gaps) are all closed or screened to prevent access by vermin, birds and other sources of contamination. | 3 Monthly
≤100 people & > 3 buildings | Roof, Surface & Groundwater | Small - Rules |  | Storage | Tanks | Check lids are secure. Check tank openings (inlets, overflows, gaps) are all closed or screened to prevent access by vermin, birds and other sources of contamination. | 3 Monthly
<100 people & ≤3 buildings | Groundwater | Acceptable Solution - Spring & Bore | 2.7 | Storage | Tanks | Check lids are secure. Check tank openings (inlets, overflows, gaps) are all closed or screened to prevent access by vermin, birds and other sources of contamination. | 3 Monthly
101 - 500 people | Surface water | Medium - Rules |  | Storage | Tanks | Check lids are secure. Check tank openings (inlets, overflows, gaps) are all closed or screened to prevent access by vermin, birds and other sources of contamination. | 3 Monthly
<100 people & ≤3 buildings | Roof | Acceptable Solution - Roof | 2.6 | Storage | Tanks | Check lids are secure. Check tank openings (inlets, overflows, gaps) are all closed or screened to prevent access by vermin, birds and other sources of contamination. | 3 Monthly
101 - 500 people | Roof & Groundwater | Medium - Rules |  | Storage | Tanks | Check lids are secure. Check tank openings (inlets, overflows, gaps) are all closed or screened to prevent access by vermin, birds and other sources of contamination. | 3 Monthly
101 - 500 people | Roof & Surface water | Medium - Rules |  | Storage | Tanks | Check lids are secure. Check tank openings (inlets, overflows, gaps) are all closed or screened to prevent access by vermin, birds and other sources of contamination. | 3 Monthly
101 - 500 people | Surface & Groundwater | Medium - Rules |  | Storage | Tanks | Check lids are secure. Check tank openings (inlets, overflows, gaps) are all closed or screened to prevent access by vermin, birds and other sources of contamination. | 3 Monthly
101 - 500 people | Roof, Surface & Groundwater | Medium - Rules |  | Storage | Tanks | Check lids are secure. Check tank openings (inlets, overflows, gaps) are all closed or screened to prevent access by vermin, birds and other sources of contamination. | 3 Monthly
≤100 people & > 3 buildings | Groundwater | Small - Rules |  | Storage | Tanks | Check lids are secure. Check tank openings (inlets, overflows, gaps) are all closed or screened to prevent access by vermin, birds and other sources of contamination. | 3 Monthly
101 - 500 people | Groundwater | Medium - Rules |  | Storage | Tanks | Check lids are secure. Check tank openings (inlets, overflows, gaps) are all closed or screened to prevent access by vermin, birds and other sources of contamination. | 3 Monthly
<100 people & ≤3 buildings | Roof | Acceptable Solution - Roof | 3.d | Source - Roof | Roof catchment | Check roof is clean and remove overhanging vegetation. | Monthly
>500 people | Roof | Large - Rules |  | Source - Roof | Roof catchment | Check roof is clean and remove overhanging vegetation. | Monthly
>500 people | Roof & Groundwater | Large - Rules |  | Source - Roof | Roof catchment | Check roof is clean and remove overhanging vegetation. | Monthly
>500 people | Roof & Surface water | Large - Rules |  | Source - Roof | Roof catchment | Check roof is clean and remove overhanging vegetation. | Monthly
>500 people | Roof, Surface & Groundwater | Large - Rules |  | Source - Roof | Roof catchment | Check roof is clean and remove overhanging vegetation. | Monthly
≤100 people & > 3 buildings | Roof | Small - Rules |  | Source - Roof | Roof catchment | Check roof is clean and remove overhanging vegetation. | Monthly
≤100 people & > 3 buildings | Roof & Groundwater | Small - Rules |  | Source - Roof | Roof catchment | Check roof is clean and remove overhanging vegetation. | Monthly
≤100 people & > 3 buildings | Roof & Surface water | Small - Rules |  | Source - Roof | Roof catchment | Check roof is clean and remove overhanging vegetation. | Monthly
≤100 people & > 3 buildings | Roof, Surface & Groundwater | Small - Rules |  | Source - Roof | Roof catchment | Check roof is clean and remove overhanging vegetation. | Monthly
101 - 500 people | Roof | Medium - Rules |  | Source - Roof | Roof catchment | Check roof is clean and remove overhanging vegetation. | Monthly
101 - 500 people | Roof & Groundwater | Medium - Rules |  | Source - Roof | Roof catchment | Check roof is clean and remove overhanging vegetation. | Monthly
101 - 500 people | Roof & Surface water | Medium - Rules |  | Source - Roof | Roof catchment | Check roof is clean and remove overhanging vegetation. | Monthly
101 - 500 people | Roof, Surface & Groundwater | Medium - Rules |  | Source - Roof | Roof catchment | Check roof is clean and remove overhanging vegetation. | Monthly
<100 people & ≤3 buildings | Groundwater | Acceptable Solution - Spring & Bore |  | Treatment | Cartridge filter | Clean cartridge filter housing. Check there are no leaks. | Monthly
>500 people | Surface water | Large - Rules | T3.63 - T3.72 | Treatment | Cartridge filter | Clean cartridge filter housing. Check there are no leaks. | Monthly
>500 people | Roof | Large - Rules | T3.63 - T3.73 | Treatment | Cartridge filter | Clean cartridge filter housing. Check there are no leaks. | Monthly
>500 people | Roof & Groundwater | Large - Rules | T3.63 - T3.73 | Treatment | Cartridge filter | Clean cartridge filter housing. Check there are no leaks. | Monthly
>500 people | Roof & Surface water | Large - Rules | T3.63 - T3.73 | Treatment | Cartridge filter | Clean cartridge filter housing. Check there are no leaks. | Monthly
>500 people | Surface & Groundwater | Large - Rules | T3.63 - T3.73 | Treatment | Cartridge filter | Clean cartridge filter housing. Check there are no leaks. | Monthly
>500 people | Roof, Surface & Groundwater | Large - Rules | T3.63 - T3.73 | Treatment | Cartridge filter | Clean cartridge filter housing. Check there are no leaks. | Monthly
>500 people | Groundwater | Large - Rules | T3.63 - T3.72 | Treatment | Cartridge filter | Clean cartridge filter housing. Check there are no leaks. | Monthly
101 - 500 people | Surface water | Medium - Rules | T2.3 - T2.9 | Treatment | Cartridge filter | Clean cartridge filter housing. Check there are no leaks. | Monthly
101 - 500 people | Roof | Medium - Rules | T2.3 - T2.9 | Treatment | Cartridge filter | Clean cartridge filter housing. Check there are no leaks. | Monthly
101 - 500 people | Roof & Groundwater | Medium - Rules | T2.3 - T2.9 | Treatment | Cartridge filter | Clean cartridge filter housing. Check there are no leaks. | Monthly
101 - 500 people | Roof & Surface water | Medium - Rules | T2.3 - T2.9 | Treatment | Cartridge filter | Clean cartridge filter housing. Check there are no leaks. | Monthly
101 - 500 people | Surface & Groundwater | Medium - Rules | T2.3 - T2.9 | Treatment | Cartridge filter | Clean cartridge filter housing. Check there are no leaks. | Monthly
101 - 500 people | Roof, Surface & Groundwater | Medium - Rules | T2.3 - T2.9 | Treatment | Cartridge filter | Clean cartridge filter housing. Check there are no leaks. | Monthly
101 - 500 people | Groundwater | Medium - Rules | T2.3 - T2.9 | Treatment | Cartridge filter | Clean cartridge filter housing. Check there are no leaks. | Monthly
≤100 people & > 3 buildings | Surface water | Small - Rules | T1.2 | Treatment | Cartridge filter | Clean cartridge filter housing. Check there are no leaks. | 3 Monthly
≤100 people & > 3 buildings | Roof | Small - Rules | T1.2 | Treatment | Cartridge filter | Clean cartridge filter housing. Check there are no leaks. | 3 Monthly
≤100 people & > 3 buildings | Roof & Groundwater | Small - Rules | T1.2 | Treatment | Cartridge filter | Clean cartridge filter housing. Check there are no leaks. | 3 Monthly
≤100 people & > 3 buildings | Roof & Surface water | Small - Rules | T1.2 | Treatment | Cartridge filter | Clean cartridge filter housing. Check there are no leaks. | 3 Monthly
≤100 people & > 3 buildings | Surface & Groundwater | Small - Rules | T1.2 | Treatment | Cartridge filter | Clean cartridge filter housing. Check there are no leaks. | 3 Monthly
≤100 people & > 3 buildings | Roof, Surface & Groundwater | Small - Rules | T1.2 | Treatment | Cartridge filter | Clean cartridge filter housing. Check there are no leaks. | 3 Monthly
≤100 people & > 3 buildings | Groundwater | Small - Rules | T1.2 | Treatment | Cartridge filter | Clean cartridge filter housing. Check there are no leaks. | 3 Monthly
>500 people | Roof & Surface water | Large - Rules |  | Source - Roof | Guttering | Check and remove any debris. | Monthly
>500 people | Roof, Surface & Groundwater | Large - Rules |  | Source - Roof | Guttering | Check and remove any debris. | Monthly
101 - 500 people | Roof | Medium - Rules |  | Source - Roof | Guttering | Check and remove any debris. | Monthly
101 - 500 people | Roof & Groundwater | Medium - Rules |  | Source - Roof | Guttering | Check and remove any debris. | Monthly
101 - 500 people | Roof & Surface water | Medium - Rules |  | Source - Roof | Guttering | Check and remove any debris. | Monthly
101 - 500 people | Roof, Surface & Groundwater | Medium - Rules |  | Source - Roof | Guttering | Check and remove any debris. | Monthly
≤100 people & > 3 buildings | Roof | Small - Rules |  | Source - Roof | Guttering | Check and remove any debris. | Monthly
≤100 people & > 3 buildings | Roof & Groundwater | Small - Rules |  | Source - Roof | Guttering | Check and remove any debris. | Monthly
>500 people | Surface water | Large - Rules | S3.3 (Table 18) | Source - Surface | Online analysers | Conductivity, pH, turbidity analysers verify and calibrate as per manufacturer's requirements. | Manufacturer’s requirements
≤100 people & > 3 buildings | Roof & Surface water | Small - Rules |  | Source - Roof | Guttering | Check and remove any debris. | Monthly
>500 people | Roof & Groundwater | Large - Rules | S3.3 (Table 18) | Source - Roof & Bore | Online analysers | Conductivity, pH, turbidity analysers verify and calibrate as per manufacturer's requirements. | Manufacturer’s requirements
>500 people | Roof & Surface water | Large - Rules | S3.3 (Table 18) | Source - Roof & Surface | Online analysers | Conductivity, pH, turbidity analysers verify and calibrate as per manufacturer's requirements. | Manufacturer’s requirements
>500 people | Surface & Groundwater | Large - Rules | S3.3 (Table 18) | Source - Bore & Surface | Online analysers | Conductivity, pH, turbidity analysers verify and calibrate as per manufacturer's requirements. | Manufacturer’s requirements
>500 people | Roof, Surface & Groundwater | Large - Rules | S3.3 (Table 18) | Source - All | Online analysers | Conductivity, pH, turbidity analysers verify and calibrate as per manufacturer's requirements. | Manufacturer’s requirements
>500 people | Groundwater | Large - Rules | S3.3 (Table 18) | Source - Bore | Online analysers | Conductivity, pH, turbidity analysers verify and calibrate as per manufacturer's requirements. | Manufacturer’s requirements
>500 people | Surface water | Large - Rules | S3.7 - S3.9 | Source - Surface | Source abstraction point | Cyanobacteria/cyanotoxin risk categorisation and monitoring as required. | Annually
>500 people | Roof & Surface water | Large - Rules | S3.7 - S3.9 | Source - Roof & Surface | Source abstraction point | Cyanobacteria/cyanotoxin risk categorisation and monitoring as required. | Annually
>500 people | Surface & Groundwater | Large - Rules | S3.7 - S3.9 | Source - Bore & Surface | Source abstraction point | Cyanobacteria/cyanotoxin risk categorisation and monitoring as required. | Annually
>500 people | Roof, Surface & Groundwater | Large - Rules | S3.7 - S3.9 | Source - All | Source abstraction point | Cyanobacteria/cyanotoxin risk categorisation and monitoring as required. | Annually
101 - 500 people | Surface water | Medium - Rules | S2.4 - S2.6 & T2.25 | Source - Surface | Source abstraction point | Cyanobacteria/cyanotoxin risk categorisation and monitoring as required. | Annually
101 - 500 people | Roof & Surface water | Medium - Rules | S2.4 - S2.6 & T2.25 | Source - Surface | Source abstraction point | Cyanobacteria/cyanotoxin risk categorisation and monitoring as required. | Annually
101 - 500 people | Surface & Groundwater | Medium - Rules | S2.4 - S2.6 & T2.25 | Source - Surface | Source abstraction point | Cyanobacteria/cyanotoxin risk categorisation and monitoring as required. | Annually
101 - 500 people | Roof, Surface & Groundwater | Medium - Rules | S2.4 - S2.6 & T2.25 | Source - Surface | Source abstraction point | Cyanobacteria/cyanotoxin risk categorisation and monitoring as required. | Annually
≤100 people & > 3 buildings | Roof, Surface & Groundwater | Small - Rules |  | Source - Roof | Guttering | Check and remove any debris. | Monthly
>500 people | Roof | Large - Rules | S3.3 (Table 18) | Source - Roof | Online analysers | Conductivity, pH, turbidity analysers verify and calibrate as per manufacturer's requirements. | Manufacturer’s requirements
>500 people | Roof & Groundwater | Large - Rules |  | Source - Roof | Raw water tank | Drain and clean out tank. | 5-yearly
>500 people | Roof & Surface water | Large - Rules |  | Source - Roof | Raw water tank | Drain and clean out tank. | 5-yearly
>500 people | Roof, Surface & Groundwater | Large - Rules |  | Source - Roof | Raw water tank | Drain and clean out tank. | 5-yearly
<100 people & ≤3 buildings | Roof | Acceptable Solution - Roof | 3.d | Source - Roof | Raw water tank | Drain and clean out tank. | 5-yearly
≤100 people & > 3 buildings | Roof & Groundwater | Small - Rules |  | Source - Roof | Raw water tank | Drain and clean out tank. | 5-yearly
≤100 people & > 3 buildings | Roof & Surface water | Small - Rules |  | Source - Roof | Raw water tank | Drain and clean out tank. | 5-yearly
≤100 people & > 3 buildings | Roof, Surface & Groundwater | Small - Rules |  | Source - Roof | Raw water tank | Drain and clean out tank. | 5-yearly
>500 people | Roof | Large - Rules |  | Source - Roof | Raw water tank | Drain and clean out tank. | 5-yearly
101 - 500 people | Roof & Groundwater | Medium - Rules |  | Source - Roof | Raw water tank | Drain and clean out tank. | 5-yearly
101 - 500 people | Roof & Surface water | Medium - Rules |  | Source - Roof | Raw water tank | Drain and clean out tank. | 5-yearly
101 - 500 people | Roof, Surface & Groundwater | Medium - Rules |  | Source - Roof | Raw water tank | Drain and clean out tank. | 5-yearly
>500 people | Surface water | Large - Rules | T3.15 (Table 22) T3.91 (Table 32) | Treatment | UV | Duty UVI sensors must be checked at least monthly against the reference sensor. If the difference between the two readings exceeds the manufacturer’s specified limits, then the Duty UVI sensor must be replaced. | Monthly
≤100 people & > 3 buildings | Roof | Small - Rules |  | Source - Roof | Raw water tank | Drain and clean out tank. | 5-yearly
>500 people | Roof & Groundwater | Large - Rules | T3.15 (Table 22) T3.91 (Table 32) | Treatment | UV | Duty UVI sensors must be checked at least monthly against the reference sensor. If the difference between the two readings exceeds the manufacturer’s specified limits, then the Duty UVI sensor must be replaced. | Monthly
>500 people | Roof & Surface water | Large - Rules | T3.15 (Table 22) T3.91 (Table 32) | Treatment | UV | Duty UVI sensors must be checked at least monthly against the reference sensor. If the difference between the two readings exceeds the manufacturer’s specified limits, then the Duty UVI sensor must be replaced. | Monthly
>500 people | Surface & Groundwater | Large - Rules | T3.15 (Table 22) T3.91 (Table 32) | Treatment | UV | Duty UVI sensors must be checked at least monthly against the reference sensor. If the difference between the two readings exceeds the manufacturer’s specified limits, then the Duty UVI sensor must be replaced. | Monthly
>500 people | Roof, Surface & Groundwater | Large - Rules | T3.15 (Table 22) T3.91 (Table 32) | Treatment | UV | Duty UVI sensors must be checked at least monthly against the reference sensor. If the difference between the two readings exceeds the manufacturer’s specified limits, then the Duty UVI sensor must be replaced. | Monthly
>500 people | Groundwater | Large - Rules | T3.15 (Table 22) T3.91 (Table 32) | Treatment | UV | Duty UVI sensors must be checked at least monthly against the reference sensor. If the difference between the two readings exceeds the manufacturer’s specified limits, then the Duty UVI sensor must be replaced. | Monthly
>500 people | Surface water | Large - Rules | T3.1 - T3.6 (Table 19) | Treatment - Chlorine disinfection | Online analysers | FAC, pH, turbidity analysers verify and calibrate as per manufacturer's requirements. | Manufacturer’s requirements
101 - 500 people | Roof | Medium - Rules |  | Source - Roof | Raw water tank | Drain and clean out tank. | 5-yearly
>500 people | Roof & Groundwater | Large - Rules | T3.1 - T3.6 (Table 19) | Treatment - Chlorine disinfection | Online analysers | FAC, pH, turbidity analysers verify and calibrate as per manufacturer's requirements. | Manufacturer’s requirements
>500 people | Roof & Surface water | Large - Rules | T3.1 - T3.6 (Table 19) | Treatment - Chlorine disinfection | Online analysers | FAC, pH, turbidity analysers verify and calibrate as per manufacturer's requirements. | Manufacturer’s requirements
>500 people | Surface & Groundwater | Large - Rules | T3.1 - T3.6 (Table 19) | Treatment - Chlorine disinfection | Online analysers | FAC, pH, turbidity analysers verify and calibrate as per manufacturer's requirements. | Manufacturer’s requirements
>500 people | Roof, Surface & Groundwater | Large - Rules | T3.1 - T3.6 (Table 19) | Treatment - Chlorine disinfection | Online analysers | FAC, pH, turbidity analysers verify and calibrate as per manufacturer's requirements. | Manufacturer’s requirements
>500 people | Groundwater | Large - Rules | T3.1 - T3.6 (Table 19) | Treatment - Chlorine disinfection | Online analysers | FAC, pH, turbidity analysers verify and calibrate as per manufacturer's requirements. | Manufacturer’s requirements
>500 people | Surface water | Large - Rules | T3.1 - T3.6 (Table 19) | Treatment - Chlorine disinfection | Flowmeter | Flowmeter check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
>500 people | Roof | Large - Rules | T3.15 (Table 22) T3.91 (Table 32) | Treatment | UV | Duty UVI sensors must be checked at least monthly against the reference sensor. If the difference between the two readings exceeds the manufacturer’s specified limits, then the Duty UVI sensor must be replaced. | Monthly
>500 people | Roof & Groundwater | Large - Rules | T3.1 - T3.6 (Table 19) | Treatment - Chlorine disinfection | Flowmeter | Flowmeter check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
>500 people | Roof & Surface water | Large - Rules | T3.1 - T3.6 (Table 19) | Treatment - Chlorine disinfection | Flowmeter | Flowmeter check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
>500 people | Surface & Groundwater | Large - Rules | T3.1 - T3.6 (Table 19) | Treatment - Chlorine disinfection | Flowmeter | Flowmeter check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
>500 people | Roof, Surface & Groundwater | Large - Rules | T3.1 - T3.6 (Table 19) | Treatment - Chlorine disinfection | Flowmeter | Flowmeter check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
>500 people | Groundwater | Large - Rules | T3.1 - T3.6 (Table 19) | Treatment - Chlorine disinfection | Flowmeter | Flowmeter check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
>500 people | Surface water | Large - Rules | T3.15 - T3.21 (Table 22) T3.85 - T3.91 (Table 32) | Treatment - UV disinfection | Flowmeter | Flowmeter check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
>500 people | Roof | Large - Rules | T3.1 - T3.6 (Table 19) | Treatment - Chlorine disinfection | Online analysers | FAC, pH, turbidity analysers verify and calibrate as per manufacturer's requirements. | Manufacturer’s requirements
>500 people | Roof & Groundwater | Large - Rules | T3.15 - T3.21 (Table 22) T3.85 - T3.91 (Table 32) | Treatment - UV disinfection | Flowmeter | Flowmeter check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
>500 people | Roof & Surface water | Large - Rules | T3.15 - T3.21 (Table 22) T3.85 - T3.91 (Table 32) | Treatment - UV disinfection | Flowmeter | Flowmeter check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
>500 people | Surface & Groundwater | Large - Rules | T3.15 - T3.21 (Table 22) T3.85 - T3.91 (Table 32) | Treatment - UV disinfection | Flowmeter | Flowmeter check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
>500 people | Roof, Surface & Groundwater | Large - Rules | T3.15 - T3.21 (Table 22) T3.85 - T3.91 (Table 32) | Treatment - UV disinfection | Flowmeter | Flowmeter check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
>500 people | Groundwater | Large - Rules | T3.15 - T3.21 (Table 22) T3.85 - T3.91 (Table 32) | Treatment - UV disinfection | Flowmeter | Flowmeter check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
>500 people | Surface water | Large - Rules | D3.12 - D3.18 | Storage | Tanks | Follow water storage management plan, including the following: Check lids are secure. Check tank openings (inlets, overflows, gaps) are all closed or screened to prevent access by vermin, birds and other sources of contamination. | 3 Monthly
>500 people | Roof | Large - Rules | T3.1 - T3.6 (Table 19) | Treatment - Chlorine disinfection | Flowmeter | Flowmeter check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
>500 people | Roof & Groundwater | Large - Rules | D3.12 - D3.19 | Storage | Tanks | Follow water storage management plan, including the following: Check lids are secure. Check tank openings (inlets, overflows, gaps) are all closed or screened to prevent access by vermin, birds and other sources of contamination. | 3 Monthly
>500 people | Roof & Surface water | Large - Rules | D3.12 - D3.19 | Storage | Tanks | Follow water storage management plan, including the following: Check lids are secure. Check tank openings (inlets, overflows, gaps) are all closed or screened to prevent access by vermin, birds and other sources of contamination. | 3 Monthly
>500 people | Surface & Groundwater | Large - Rules | D3.12 - D3.19 | Storage | Tanks | Follow water storage management plan, including the following: Check lids are secure. Check tank openings (inlets, overflows, gaps) are all closed or screened to prevent access by vermin, birds and other sources of contamination. | 3 Monthly
>500 people | Roof, Surface & Groundwater | Large - Rules | D3.12 - D3.19 | Storage | Tanks | Follow water storage management plan, including the following: Check lids are secure. Check tank openings (inlets, overflows, gaps) are all closed or screened to prevent access by vermin, birds and other sources of contamination. | 3 Monthly
>500 people | Groundwater | Large - Rules | D3.12 - D3.17 | Storage | Tanks | Follow water storage management plan, including the following: Check lids are secure. Check tank openings (inlets, overflows, gaps) are all closed or screened to prevent access by vermin, birds and other sources of contamination. | 3 Monthly
>500 people | Roof & Groundwater | Large - Rules | 4.9.2 | Source - Roof & Bore | Bore | Inspect bore head and confirm sanitary bore head requirements if applicable. Repair any defects. | Monthly
>500 people | Surface & Groundwater | Large - Rules | 4.9.2 | Source - Bore & Surface | Bore | Inspect bore head and confirm sanitary bore head requirements if applicable. Repair any defects. | Monthly
>500 people | Roof, Surface & Groundwater | Large - Rules | 4.9.2 | Source - All | Bore | Inspect bore head and confirm sanitary bore head requirements if applicable. Repair any defects. | Monthly
>500 people | Groundwater | Large - Rules | 4.9.2 | Source - Bore | Bore | Inspect bore head and confirm sanitary bore head requirements if applicable. Repair any defects. | Monthly
>500 people | Roof | Large - Rules | T3.15 - T3.21 (Table 22) T3.85 - T3.91 (Table 32) | Treatment - UV disinfection | Flowmeter | Flowmeter check and maintain as per manufacturer's requirements. | Manufacturer’s requirements
>500 people | Roof | Large - Rules | D3.12 - D3.19 | Storage | Tanks | Follow water storage management plan, including the following: Check lids are secure. Check tank openings (inlets, overflows, gaps) are all closed or screened to prevent access by vermin, birds and other sources of contamination. | 3 Monthly
<100 people & ≤3 buildings | Roof | Acceptable Solution - Roof |  | Source - Roof | Leaf screen | Lift the screen out, empty and replace when cleaned. | 6 Monthly
>500 people | Roof & Groundwater | Large - Rules |  | Source - Roof | Leaf screen | Lift the screen out, empty and replace when cleaned. | 6 Monthly
>500 people | Roof & Surface water | Large - Rules |  | Source - Roof | Leaf screen | Lift the screen out, empty and replace when cleaned. | 6 Monthly
>500 people | Roof, Surface & Groundwater | Large - Rules |  | Source - Roof | Leaf screen | Lift the screen out, empty and replace when cleaned. | 6 Monthly
>500 people | Roof | Large - Rules |  | Source - Roof | Leaf screen | Lift the screen out, empty and replace when cleaned. | 6 Monthly
101 - 500 people | Roof & Groundwater | Medium - Rules |  | Source - Roof | Leaf screen | Lift the screen out, empty and replace when cleaned. | 6 Monthly
101 - 500 people | Roof & Surface water | Medium - Rules |  | Source - Roof | Leaf screen | Lift the screen out, empty and replace when cleaned. | 6 Monthly
101 - 500 people | Roof, Surface & Groundwater | Medium - Rules |  | Source - Roof | Leaf screen | Lift the screen out, empty and replace when cleaned. | 6 Monthly
101 - 500 people | Roof | Medium - Rules |  | Source - Roof | Leaf screen | Lift the screen out, empty and replace when cleaned. | 6 Monthly
≤100 people & > 3 buildings | Roof & Groundwater | Small - Rules |  | Source - Roof | Leaf screen | Lift the screen out, empty and replace when cleaned. | 6 Monthly
≤100 people & > 3 buildings | Roof & Surface water | Small - Rules |  | Source - Roof | Leaf screen | Lift the screen out, empty and replace when cleaned. | 6 Monthly
≤100 people & > 3 buildings | Roof, Surface & Groundwater | Small - Rules |  | Source - Roof | Leaf screen | Lift the screen out, empty and replace when cleaned. | 6 Monthly
<100 people & ≤3 buildings | Groundwater | Acceptable Solution - Spring & Bore |  | Treatment | UV | Record UV lamp hours. Check UV dose is within range. If not arrange for service. | Monthly
>500 people | Surface water | Large - Rules |  | Treatment | UV | Record UV lamp hours. Check UV dose is within range. If not arrange for service. | Monthly
≤100 people & > 3 buildings | Roof | Small - Rules |  | Source - Roof | Leaf screen | Lift the screen out, empty and replace when cleaned. | 6 Monthly
>500 people | Roof & Groundwater | Large - Rules |  | Treatment | UV | Record UV lamp hours. Check UV dose is within range. If not arrange for service. | Monthly
>500 people | Roof & Surface water | Large - Rules |  | Treatment | UV | Record UV lamp hours. Check UV dose is within range. If not arrange for service. | Monthly
>500 people | Surface & Groundwater | Large - Rules |  | Treatment | UV | Record UV lamp hours. Check UV dose is within range. If not arrange for service. | Monthly
>500 people | Roof, Surface & Groundwater | Large - Rules |  | Treatment | UV | Record UV lamp hours. Check UV dose is within range. If not arrange for service. | Monthly
>500 people | Groundwater | Large - Rules |  | Treatment | UV | Record UV lamp hours. Check UV dose is within range. If not arrange for service. | Monthly
≤100 people & > 3 buildings | Surface water | Small - Rules |  | Treatment | UV | Record UV lamp hours. Check UV dose is within range. If not arrange for service. | Monthly
>500 people | Roof | Large - Rules |  | Treatment | UV | Record UV lamp hours. Check UV dose is within range. If not arrange for service. | Monthly
≤100 people & > 3 buildings | Roof & Groundwater | Small - Rules |  | Treatment | UV | Record UV lamp hours. Check UV dose is within range. If not arrange for service. | Monthly
≤100 people & > 3 buildings | Roof & Surface water | Small - Rules |  | Treatment | UV | Record UV lamp hours. Check UV dose is within range. If not arrange for service. | Monthly
≤100 people & > 3 buildings | Surface & Groundwater | Small - Rules |  | Treatment | UV | Record UV lamp hours. Check UV dose is within range. If not arrange for service. | Monthly
≤100 people & > 3 buildings | Roof, Surface & Groundwater | Small - Rules |  | Treatment | UV | Record UV lamp hours. Check UV dose is within range. If not arrange for service. | Monthly
≤100 people & > 3 buildings | Roof | Small - Rules |  | Treatment | UV | Record UV lamp hours. Check UV dose is within range. If not arrange for service. | Monthly
101 - 500 people | Roof | Medium - Rules | T2.10 - T2.17 | Treatment | UV | Record UV lamp hours. Check UV dose is within range. If not arrange for service. | Monthly
101 - 500 people | Roof & Groundwater | Medium - Rules | T2.10 - T2.17 | Treatment | UV | Record UV lamp hours. Check UV dose is within range. If not arrange for service. | Monthly
101 - 500 people | Roof & Surface water | Medium - Rules | T2.10 - T2.17 | Treatment | UV | Record UV lamp hours. Check UV dose is within range. If not arrange for service. | Monthly
101 - 500 people | Surface & Groundwater | Medium - Rules | T2.10 - T2.17 | Treatment | UV | Record UV lamp hours. Check UV dose is within range. If not arrange for service. | Monthly
101 - 500 people | Roof, Surface & Groundwater | Medium - Rules | T2.10 - T2.17 | Treatment | UV | Record UV lamp hours. Check UV dose is within range. If not arrange for service. | Monthly
≤100 people & > 3 buildings | Groundwater | Small - Rules |  | Treatment | UV | Record UV lamp hours. Check UV dose is within range. If not arrange for service. | Monthly
<100 people & ≤3 buildings | Roof | Acceptable Solution - Roof |  | Treatment | UV | Record UV lamp hours. Check UV dose is within range. If not arrange for service. | Monthly
<100 people & ≤3 buildings | Groundwater | Acceptable Solution - Spring & Bore |  | Treatment | Cartridge filter | Replace filter cartridge. | 6 Monthly
≤100 people & > 3 buildings | Surface water | Small - Rules | T1.2 | Treatment | Cartridge filter | Replace filter cartridge. | 6 Monthly
<100 people & ≤3 buildings | Roof | Acceptable Solution - Roof |  | Treatment | Cartridge filter | Replace filter cartridge. | 6 Monthly
≤100 people & > 3 buildings | Roof & Groundwater | Small - Rules | T1.2 & T1.5 | Treatment | Cartridge filter | Replace filter cartridge. | 6 Monthly
≤100 people & > 3 buildings | Roof & Surface water | Small - Rules | T1.2 & T1.5 | Treatment | Cartridge filter | Replace filter cartridge. | 6 Monthly
≤100 people & > 3 buildings | Surface & Groundwater | Small - Rules | T1.2 | Treatment | Cartridge filter | Replace filter cartridge. | 6 Monthly
≤100 people & > 3 buildings | Roof, Surface & Groundwater | Small - Rules | T1.2 & T1.5 | Treatment | Cartridge filter | Replace filter cartridge. | 6 Monthly
≤100 people & > 3 buildings | Groundwater | Small - Rules | T1.2 | Treatment | Cartridge filter | Replace filter cartridge. | 6 Monthly
<100 people & ≤3 buildings | Groundwater | Acceptable Solution - Spring & Bore |  | Treatment | UV | Replace UV lamp and sleeve as recommended by manufacturer. | Annually
>500 people | Surface water | Large - Rules | T3.85 - T3.91 | Treatment | UV | Replace UV lamp and sleeve as recommended by manufacturer. | Annually
≤100 people & > 3 buildings | Roof | Small - Rules | T1.5 | Treatment | Cartridge filter | Replace filter cartridge. | 6 Monthly
>500 people | Roof & Groundwater | Large - Rules | T3.85 - T3.92 | Treatment | UV | Replace UV lamp and sleeve as recommended by manufacturer. | Annually
>500 people | Roof & Surface water | Large - Rules | T3.85 - T3.92 | Treatment | UV | Replace UV lamp and sleeve as recommended by manufacturer. | Annually
>500 people | Surface & Groundwater | Large - Rules | T3.85 - T3.92 | Treatment | UV | Replace UV lamp and sleeve as recommended by manufacturer. | Annually
>500 people | Roof, Surface & Groundwater | Large - Rules | T3.85 - T3.92 | Treatment | UV | Replace UV lamp and sleeve as recommended by manufacturer. | Annually
>500 people | Groundwater | Large - Rules | T3.85 - T3.91 | Treatment | UV | Replace UV lamp and sleeve as recommended by manufacturer. | Annually
≤100 people & > 3 buildings | Surface water | Small - Rules | T1.5 & T1.6 | Treatment | UV | Replace UV lamp and sleeve as recommended by manufacturer. | Annually
>500 people | Roof | Large - Rules | T3.85 - T3.92 | Treatment | UV | Replace UV lamp and sleeve as recommended by manufacturer. | Annually
≤100 people & > 3 buildings | Roof & Groundwater | Small - Rules | T1.5 & T1.6 | Treatment | UV | Replace UV lamp and sleeve as recommended by manufacturer. | Annually
≤100 people & > 3 buildings | Roof & Surface water | Small - Rules | T1.5 & T1.6 | Treatment | UV | Replace UV lamp and sleeve as recommended by manufacturer. | Annually
≤100 people & > 3 buildings | Surface & Groundwater | Small - Rules | T1.5 & T1.6 | Treatment | UV | Replace UV lamp and sleeve as recommended by manufacturer. | Annually
≤100 people & > 3 buildings | Roof, Surface & Groundwater | Small - Rules | T1.5 & T1.6 | Treatment | UV | Replace UV lamp and sleeve as recommended by manufacturer. | Annually
101 - 500 people | Surface water | Medium - Rules | T2.10 - T2.17 | Treatment | UV | Replace UV lamp and sleeve as recommended by manufacturer. | Annually
≤100 people & > 3 buildings | Roof | Small - Rules | T1.5 & T1.6 | Treatment | UV | Replace UV lamp and sleeve as recommended by manufacturer. | Annually
101 - 500 people | Roof & Groundwater | Medium - Rules | T2.10 - T2.17 | Treatment | UV | Replace UV lamp and sleeve as recommended by manufacturer. | Annually
101 - 500 people | Roof & Surface water | Medium - Rules | T2.10 - T2.17 | Treatment | UV | Replace UV lamp and sleeve as recommended by manufacturer. | Annually
101 - 500 people | Surface & Groundwater | Medium - Rules | T2.10 - T2.17 | Treatment | UV | Replace UV lamp and sleeve as recommended by manufacturer. | Annually
101 - 500 people | Roof, Surface & Groundwater | Medium - Rules | T2.10 - T2.17 | Treatment | UV | Replace UV lamp and sleeve as recommended by manufacturer. | Annually
≤100 people & > 3 buildings | Groundwater | Small - Rules | T1.5 & T1.6 | Treatment | UV | Replace UV lamp and sleeve as recommended by manufacturer. | Annually
101 - 500 people | Groundwater | Medium - Rules | T2.10 - T2.17 | Treatment | UV | Replace UV lamp and sleeve as recommended by manufacturer. | Annually
>500 people | Surface water | Large - Rules | T3.15 (Table 22) T3.91 (Table 32) | Treatment | UV | Standardise UVI sensor. | Annually
101 - 500 people | Roof | Medium - Rules | T2.10 - T2.17 | Treatment | UV | Replace UV lamp and sleeve as recommended by manufacturer. | Annually
>500 people | Roof & Groundwater | Large - Rules | T3.15 (Table 22) T3.91 (Table 32) | Treatment | UV | Standardise UVI sensor. | Annually
>500 people | Roof & Surface water | Large - Rules | T3.15 (Table 22) T3.91 (Table 32) | Treatment | UV | Standardise UVI sensor. | Annually
>500 people | Surface & Groundwater | Large - Rules | T3.15 (Table 22) T3.91 (Table 32) | Treatment | UV | Standardise UVI sensor. | Annually
>500 people | Roof, Surface & Groundwater | Large - Rules | T3.15 (Table 22) T3.91 (Table 32) | Treatment | UV | Standardise UVI sensor. | Annually
>500 people | Groundwater | Large - Rules | T3.15 (Table 22) T3.91 (Table 32) | Treatment | UV | Standardise UVI sensor. | Annually
≤100 people & > 3 buildings | Groundwater | Small - Rules | D1.2 | Distribution | Backflow prevention device | Test all testable backflow prevention devices installed. | Annually
≤100 people & > 3 buildings | Surface water | Small - Rules | D1.2 | Distribution | Backflow prevention device | Test all testable backflow prevention devices installed. | Annually
<100 people & ≤3 buildings | Roof | Acceptable Solution - Roof | 3.f | Treatment | UV | Replace UV lamp and sleeve as recommended by manufacturer. | Annually
≤100 people & > 3 buildings | Roof & Groundwater | Small - Rules | D1.2 | Distribution | Backflow prevention device | Test all testable backflow prevention devices installed. | Annually
≤100 people & > 3 buildings | Roof & Surface water | Small - Rules | D1.2 | Distribution | Backflow prevention device | Test all testable backflow prevention devices installed. | Annually
≤100 people & > 3 buildings | Surface & Groundwater | Small - Rules | D1.2 | Distribution | Backflow prevention device | Test all testable backflow prevention devices installed. | Annually
≤100 people & > 3 buildings | Roof, Surface & Groundwater | Small - Rules | D1.2 | Distribution | Backflow prevention device | Test all testable backflow prevention devices installed. | Annually
>500 people | Roof | Large - Rules | T3.15 (Table 22) T3.91 (Table 32) | Treatment | UV | Standardise UVI sensor. | Annually
<100 people & ≤3 buildings | Groundwater | Acceptable Solution - Spring & Bore | 2.1.c | Source - Bore | Backflow prevention device | Test all testable backflow prevention devices installed. | Annually
>500 people | Surface water | Large - Rules | D3.4 | Distribution | Backflow prevention device | Test all testable backflow prevention devices installed. Keep a register of the location of all point of supply testable backflow protection devices, device types, assessed risk level and the results of testing of all devices. | Annually
>500 people | Surface water | Large - Rules | D3.5 | Distribution | Backflow prevention device | Test all testable backflow prevention devices installed. Keep a register of the location of all point of supply testable backflow protection devices, device types, assessed risk level and the results of testing of all devices. | Annually
>500 people | Roof & Groundwater | Large - Rules | D3.5 | Distribution | Backflow prevention device | Test all testable backflow prevention devices installed. Keep a register of the location of all point of supply testable backflow protection devices, device types, assessed risk level and the results of testing of all devices. | Annually
>500 people | Roof & Surface water | Large - Rules | D3.5 | Distribution | Backflow prevention device | Test all testable backflow prevention devices installed. Keep a register of the location of all point of supply testable backflow protection devices, device types, assessed risk level and the results of testing of all devices. | Annually
>500 people | Surface & Groundwater | Large - Rules | D3.5 | Distribution | Backflow prevention device | Test all testable backflow prevention devices installed. Keep a register of the location of all point of supply testable backflow protection devices, device types, assessed risk level and the results of testing of all devices. | Annually
>500 people | Roof, Surface & Groundwater | Large - Rules | D3.5 | Distribution | Backflow prevention device | Test all testable backflow prevention devices installed. Keep a register of the location of all point of supply testable backflow protection devices, device types, assessed risk level and the results of testing of all devices. | Annually
>500 people | Groundwater | Large - Rules | D3.4 | Distribution | Backflow prevention device | Test all testable backflow prevention devices installed. Keep a register of the location of all point of supply testable backflow protection devices, device types, assessed risk level and the results of testing of all devices. | Annually
101 - 500 people | Surface water | Medium - Rules | T2.17 | Treatment | UV | The UVI sensor must be referenced against a new sensor annually and should be replaced if it reads levels different to the new sensor that are outside the manufacturer’s recommendation. | Annually
<100 people & ≤3 buildings | Roof | Acceptable Solution - Roof |  | Distribution | Backflow prevention device | Test all testable backflow prevention devices installed. | Annually
101 - 500 people | Roof & Groundwater | Medium - Rules | T2.17 | Treatment | UV | The UVI sensor must be referenced against a new sensor annually and should be replaced if it reads levels different to the new sensor that are outside the manufacturer’s recommendation. | Annually
101 - 500 people | Roof & Surface water | Medium - Rules | T2.17 | Treatment | UV | The UVI sensor must be referenced against a new sensor annually and should be replaced if it reads levels different to the new sensor that are outside the manufacturer’s recommendation. | Annually
101 - 500 people | Surface & Groundwater | Medium - Rules | T2.17 | Treatment | UV | The UVI sensor must be referenced against a new sensor annually and should be replaced if it reads levels different to the new sensor that are outside the manufacturer’s recommendation. | Annually
101 - 500 people | Roof, Surface & Groundwater | Medium - Rules | T2.17 | Treatment | UV | The UVI sensor must be referenced against a new sensor annually and should be replaced if it reads levels different to the new sensor that are outside the manufacturer’s recommendation. | Annually
101 - 500 people | Groundwater | Medium - Rules | T2.17 | Treatment | UV | The UVI sensor must be referenced against a new sensor annually and should be replaced if it reads levels different to the new sensor that are outside the manufacturer’s recommendation. | Annually
≤100 people & > 3 buildings | Surface water | Small - Rules | S1.4 | Source - Surface | Source abstraction point | The water and area within 50 metres of a surface water intake, must be visually inspected for the presence of benthic cyanobacteria mats and planktonic cyanobacterial growth. If there is evidence of cyanobacterial growth, steps must be taken to evaluate the cyanotoxin risk to consumers. If there is a risk of supplying water with cyanotoxins that exceed MAVs, abstraction of water must be discontinued until the risk is no longer present. | Monthly - between October and May (inclusive)
≤100 people & > 3 buildings | Roof & Surface water | Small - Rules | S1.4 | Source - Surface | Source abstraction point | The water and area within 50 metres of a surface water intake, must be visually inspected for the presence of benthic cyanobacteria mats and planktonic cyanobacterial growth. If there is evidence of cyanobacterial growth, steps must be taken to evaluate the cyanotoxin risk to consumers. If there is a risk of supplying water with cyanotoxins that exceed MAVs, abstraction of water must be discontinued until the risk is no longer present. | Monthly - between October and May (inclusive)
≤100 people & > 3 buildings | Surface & Groundwater | Small - Rules | S1.4 | Source - Surface | Source abstraction point | The water and area within 50 metres of a surface water intake, must be visually inspected for the presence of benthic cyanobacteria mats and planktonic cyanobacterial growth. If there is evidence of cyanobacterial growth, steps must be taken to evaluate the cyanotoxin risk to consumers. If there is a risk of supplying water with cyanotoxins that exceed MAVs, abstraction of water must be discontinued until the risk is no longer present. | Monthly - between October and May (inclusive)
≤100 people & > 3 buildings | Roof, Surface & Groundwater | Small - Rules | S1.4 | Source - Surface | Source abstraction point | The water and area within 50 metres of a surface water intake, must be visually inspected for the presence of benthic cyanobacteria mats and planktonic cyanobacterial growth. If there is evidence of cyanobacterial growth, steps must be taken to evaluate the cyanotoxin risk to consumers. If there is a risk of supplying water with cyanotoxins that exceed MAVs, abstraction of water must be discontinued until the risk is no longer present. | Monthly - between October and May (inclusive)
>500 people | Surface water | Large - Rules | T3.72 (Table 28) | Treatment - Cartridge Filtration | Online analysers | Turbidity and pressure anlysers verify and calibrate as per manufacturer's requirements. | Manufacturer’s requirements
≤100 people & > 3 buildings | Roof | Small - Rules | D1.2 | Distribution | Backflow prevention device | Test all testable backflow prevention devices installed. | Annually
>500 people | Roof & Groundwater | Large - Rules | T3.72 (Table 28) | Treatment - Cartridge Filtration | Online analysers | Turbidity and pressure anlysers verify and calibrate as per manufacturer's requirements. | Manufacturer’s requirements
>500 people | Roof & Surface water | Large - Rules | T3.72 (Table 28) | Treatment - Cartridge Filtration | Online analysers | Turbidity and pressure anlysers verify and calibrate as per manufacturer's requirements. | Manufacturer’s requirements
>500 people | Surface & Groundwater | Large - Rules | T3.72 (Table 28) | Treatment - Cartridge Filtration | Online analysers | Turbidity and pressure anlysers verify and calibrate as per manufacturer's requirements. | Manufacturer’s requirements
>500 people | Roof, Surface & Groundwater | Large - Rules | T3.72 (Table 28) | Treatment - Cartridge Filtration | Online analysers | Turbidity and pressure anlysers verify and calibrate as per manufacturer's requirements. | Manufacturer’s requirements
>500 people | Groundwater | Large - Rules | T3.72 (Table 28) | Treatment - Cartridge Filtration | Online analysers | Turbidity and pressure anlysers verify and calibrate as per manufacturer's requirements. | Manufacturer’s requirements
>500 people | Surface water | Large - Rules | T3.15 - T3.21 (Table 22) T3.85 - T3.91 (Table 32) | Treatment - UV disinfection | Online analysers | UVT, turbidity, UVI or dose analysers verify and calibrate as per manufacturer's requirements. | Manufacturer’s requirements
101 - 500 people | Roof | Medium - Rules | T2.17 | Treatment | UV | The UVI sensor must be referenced against a new sensor annually and should be replaced if it reads levels different to the new sensor that are outside the manufacturer’s recommendation. | Annually
>500 people | Roof & Groundwater | Large - Rules | T3.15 - T3.21 (Table 22) T3.85 - T3.91 (Table 32) | Treatment - UV disinfection | Online analysers | UVT, turbidity, UVI or dose analysers verify and calibrate as per manufacturer's requirements. | Manufacturer’s requirements
>500 people | Roof & Surface water | Large - Rules | T3.15 - T3.21 (Table 22) T3.85 - T3.91 (Table 32) | Treatment - UV disinfection | Online analysers | UVT, turbidity, UVI or dose analysers verify and calibrate as per manufacturer's requirements. | Manufacturer’s requirements
>500 people | Surface & Groundwater | Large - Rules | T3.15 - T3.21 (Table 22) T3.85 - T3.91 (Table 32) | Treatment - UV disinfection | Online analysers | UVT, turbidity, UVI or dose analysers verify and calibrate as per manufacturer's requirements. | Manufacturer’s requirements
>500 people | Roof, Surface & Groundwater | Large - Rules | T3.15 - T3.21 (Table 22) T3.85 - T3.91 (Table 32) | Treatment - UV disinfection | Online analysers | UVT, turbidity, UVI or dose analysers verify and calibrate as per manufacturer's requirements. | Manufacturer’s requirements
>500 people | Groundwater | Large - Rules | T3.15 - T3.21 (Table 22) T3.85 - T3.91 (Table 32) | Treatment - UV disinfection | Online analysers | UVT, turbidity, UVI or dose analysers verify and calibrate as per manufacturer's requirements. | Manufacturer’s requirements
>500 people | Roof | Large - Rules | T3.72 (Table 28) | Treatment - Cartridge Filtration | Online analysers | Turbidity and pressure anlysers verify and calibrate as per manufacturer's requirements. | Manufacturer’s requirements
>500 people | Roof | Large - Rules | T3.15 - T3.21 (Table 22) T3.85 - T3.91 (Table 32) | Treatment - UV disinfection | Online analysers | UVT, turbidity, UVI or dose analysers verify and calibrate as per manufacturer's requirements. | Manufacturer’s requirements
This shape represents a table slicer. Table slicers are not supported in this version of Excel. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.
This shape represents a table slicer. Table slicers are not supported in this version of Excel. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.
This shape represents a table slicer. Table slicers are not supported in this version of Excel. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.
This shape represents a table slicer. Table slicers are not supported in this version of Excel. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.
This shape represents a table slicer. Table slicers are not supported in this version of Excel. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.
This shape represents a table slicer. Table slicers are not supported in this version of Excel. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.

## Data Capture ≤100 people
Water Data Capture ≤100 people
Deselect equipment / systems that are not relevant to the school:
| Maintenance | Equipment/System | Frequency | Example
| Date |  |  | 2022-12-01
| Name |  |  | John
| Check roof is clean and remove overhanging vegetation. | Roof catchment | Monthly | Done
| Check and remove any debris. | Guttering | Monthly | Done
| Lift the screen out, empty and replace when cleaned. | Leaf screen | 6 Monthly | Done
| The water and area within 50 metres of a surface water intake, must be visually inspected for the presence of benthic cyanobacteria mats and planktonic cyanobacterial growth. If there is evidence of cyanobacterial growth, steps must be taken to evaluate the cyanotoxin risk to consumers. If there is a risk of supplying water with cyanotoxins that exceed MAVs, abstraction of water must be discontinued until the risk is no longer present. | Surface water | Monthly - between October and May (inclusive) | No growth
| Check fencing excludes animals and bore head excludes stormwater. Repair any defects. | Bore | Monthly | Done
| Supply pump check (Date last maintained or state what was done). | All sources | Manufacturer’s requirements | 2022-08-01
| Raw water tank: Check calmed bottom inlet and floating off take (Date last checked). | Surface water | Annually | 2022-08-01
| Media filter: Check and maintain as per manufacturer's requirements (Date last maintained or state what was done). | Media filter | Manufacturer’s requirements | 2022-08-01
| Clean cartridge filter housing. Check there are no leaks. | Cartridge filter | 3 Monthly | Cleaned. No leaks.
| Replace filter cartridge (Date last replaced). | Cartridge filter | 6 Monthly | 2022-06-01
| Replace UV lamp and sleeve as recommended by manufacturer (Date last replaced). | UV | Annually | 2022-06-01
| Record UV lamp hours. Check UV dose is within range. If not arrange for service. | UV | Monthly | 4000 hrs
| Check lids are secure. Check tank openings (inlets, overflows, gaps) are all closed or screened to prevent access by vermin, birds and other sources of contamination. | Water tanks | 3 Monthly | Done
| Assess the distribution system for backflow risk (Date last checked). | Distribution end point | Annually | 2022-06-01
| Test all testable backflow prevention devices (date and result of last test) | Distribution end point | Annually | Passed 12/08/2022
| Clean first flush diverters. | First flush diverter | Monthly | Done
| Drain and clean tank out. | Raw water tank (roof supplies) | 5-yearly | 2019-09-07
| Monitoring | Equipment/System | Frequency | Example
| Date |  |  | 2022-12-01
| Name |  |  | John
| E. coli (MPN/100 mL) | All sources | 3 Monthly | 100
| Total Coliforms (MPN/100 mL) | All sources | 3 Monthly | 200
| Arsenic, boron, nitrate, iron, manganese monitoring (Date last done) | All sources | 3 Yearly | 2022-06-01
| Cadmium, copper, zinc, lead, benzo[a]pyrene (In winter – June, July, or August) monitoring (Date last done) | Roof source | 3 Yearly | 2022-06-01
| E. coli (MPN/100 mL) | Distribution end point | Monthly | <1
| Total Coliforms (MPN/100 mL) | Distribution end point | Monthly | <1
| Turbidity (NTU) | Distribution end point | Monthly | 0.2
This shape represents a table slicer. Table slicers are not supported in this version of Excel. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.

## Data Capture 101-500 people
Water Data Capture 101-500 people
Deselect equipment / systems that are not relevant to the school:
Choose distribution end point (networked supply) if the water supply is to more than 10 buildings and/or non-Crown owned properties
| Maintenance | Equipment/System | Frequency | Example
| Date |  |  | 2022-12-01
| Name |  |  | John
| Check roof is clean and remove overhanging vegetation. | Roof catchment | Monthly | Done
| Check and remove any debris. Clean leaf screens and first flush diverters. | Guttering | Monthly | Done
| Lift the screen out, empty and replace when cleaned. | Leaf screen | 6 Monthly | Done
| Cyanobacteria/cyanotoxin categorisation and monitoring as required (Date last done). | Surface water | Annually | 2022-06-01
| Check fencing excludes animals and bore head excludes stormwater. Repair any defects. | Bore | Monthly | Done
| Supply pump check (Date last maintained or state what was done). | All sources | Manufacturer’s requirements | 2022-08-01
| Raw water tank: Check calmed bottom inlet and floating out take (Date last checked). | Surface water | Annually | 2022-08-01
| Media filter: Check and maintain as per manufacturer's requirements (Date last maintained or state what was done). | Media filter | Manufacturer’s requirements | 2022-08-01
| Membrane filter: Check and maintain as per manufacturer's requirements (Date last maintained or state what was done). | Membrane filter | Manufacturer’s requirements | 2022-08-01
| Clean cartridge filter housing. Check there are no leaks. | Cartridge filter | Monthly | Cleaned. No leaks.
| Check differential pressure across cartridge filters. Replace as per manufacturer's recommendations or if pressure and water quality indicate necessary. | Cartridge filter | Monthly | 7 kPa
| Replace filter cartridge (Date last replaced). | Cartridge filter | 6 Monthly | 2022-06-01
| Replace UV lamp and sleeve as recommended by manufacturer (Date last replaced). | UV | Annually | 2022-06-01
| Record UV lamp hours. Check UV dose is within range. If not arrange for service. | UV | Monthly | 4000 hrs
| The UVI sensor must be referenced against a new sensor annually and should be replaced if it reads levels different to the new sensor that are outside the manufacturer’s recommendation. | UV | Annually | 2022-06-01
| Check lids are secure. Check tank openings (inlets, overflows, gaps) are all closed or screened to prevent access by vermin, birds and other sources of contamination. | Water tanks | 3 Monthly | Done
| Assess the distribution system for backflow risk (Date last checked). | Distribution end point | Annually | 2022-06-01
| Test all testable backflow prevention devices (date and result of last test) | Distribution end point | Annually | Passed 12/08/2022
| Clean first flush diverters. | First flush diverter | Monthly | Done
| Drain and clean tank out. | Raw water tank (roof supplies) | 5-yearly | 2019-09-07
| Check chemical stock levels and re-stock if required. Maintain as per manufacturer's requirements. | Chlorination | Monthly | 2022-06-01
Example
Monitoring | Date |  |  | 2022-12-01
| Name |  |  | John
| E. coli (MPN/100 mL) | All sources | Monthly | 100
| Total Coliforms (MPN/100 mL) | All sources | Monthly | 200
| pH | All sources | 6 Monthly | 7.2
| Turbidity (NTU) | All sources | 6 Monthly | 2
| Iron, manganese and nitrate monitoring (Date last done) | Bore | Annually | 2022-06-01
| Arsenic and boron monitoring (Date last done) | Bore | 3 Yearly | 2022-06-01
| Iron, manganese and nitrate monitoring (Date last done) | Surface water | Annually | 2022-06-01
| Arsenic and boron monitoring (Date last done) | Surface water | 3 Yearly | 2022-06-01
| Cadmium, copper, zinc, lead, benzo[a]pyrene (In winter – June, July, or August) monitoring (Date last done) | Roof source | 3 Yearly | 2022-06-01
| E. coli (MPN/100 mL) | Treated water | Monthly | <1
| Total Coliforms (MPN/100 mL) | Treated water | Monthly | <1
| Any chemical used in the treatment process (excluding FAC) | Treated water | Monthly | Alum: 0.1 mg/L
| Turbidity (NTU), UVI or UV dose (at the reactor), FAC (in water leaving the treatment plant), pH (in water leaving the treatment plant) | Treated water | 2 per week | Record below
| UVT | Treated water | 3 Monthly
| Chlorate (if sodium hypochlorite is used) | Treated water | 3 Monthly
| FAC | Treated water | 2 per week | Record below
| E. coli (MPN/100 mL) | Distribution end point | Monthly | <1
| Total Coliforms (MPN/100 mL) | Distribution end point | Monthly | <1
| Antimony, cadmium, chromium, copper, lead, mercury, nickel, zinc (Date last done) | Distribution end point (networked supply) | Annually | 2022-06-01
Frequent testing (2 per week) | Turbidity (NTU) | Treated water | 2 per week | 0.1
| UVI or UV dose (at the reactor) | Treated water | 2 per week | 40
| FAC | Treated water | 2 per week | 0.3
| pH | Treated water | 2 per week | 7
| FAC | Distribution end point (networked supply) | 2 per week | 0.3
This shape represents a table slicer. Table slicers are not supported in this version of Excel. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.

## Data Capture >500 people
Water Data Capture >500 people
Deselect equipment / systems that are not relevant to the school:
Choose distribution end point (networked supply) if the water supply is to more than 10 buildings and/or non-Crown owned properties
This checklist assumes that bacterial disinfection is achieved via UV disinfection, and that protozoal inactivation is achieved with cartridge filtration and UV disinfection. Different monitoring requirements apply if other treatment methods are used.
| Maintenance | Equipment/System | Frequency | Example
| Date |  |  | 2022-12-01
| Name |  |  | John
| Check roof is clean and remove overhanging vegetation. | Roof catchment | Monthly | Checked
| Check and remove any debris. Clean leaf screens and first flush diverters. | Guttering | Monthly | Checked
| Lift the screen out, empty and replace when cleaned. | Leaf screen | 6 Monthly | Done
| Cyanobacteria/cyanotoxin categorisation and monitoring as required (Date last done). | Surface water | Annually | 2022-06-01
| Inspect bore head and confirm sanitary bore head requirements if applicable. Repair any defects. | Bore | Monthly | Inspected
| Supply pump check (Date last maintained or state what was done). | All sources | Manufacturer’s requirements | 2022-08-01
| Raw water tank: Check calmed bottom inlet and floating out take (Date last checked). | Surface water | Annually | 2022-08-01
| Conductivity, pH, turbidity analysers verify and calibrate as per manufacturer's requirements. | Online Analysers | Manufacturer’s requirements | Calibrated
| Flowmeter check and maintain as per manufacturer's requirements (Date last maintained or state what was done). | Flowmeter | Manufacturer’s requirements | 2022-08-01
| Media filter: Check and maintain as per manufacturer's requirements (Date last maintained or state what was done). | Media filter | Manufacturer’s requirements | 2022-08-01
| Membrane filter: Check and maintain as per manufacturer's requirements (Date last maintained or state what was done). | Membrane filter | Manufacturer’s requirements | 2022-08-01
| Clean cartridge filter housing. Check there are no leaks. | Cartridge filter | Monthly | Cleaned. No leaks.
| Check differential pressure across cartridge filters. Replace as per manufacturer's recommendations or if pressure and water quality indicate necessary. | Cartridge filter | Monthly | 7 kPa
| Replace filter cartridge (Date last replaced). | Cartridge filter | 6 Monthly | 2022-06-01
| Replace UV lamp and sleeve as recommended by manufacturer (Date last replaced). | UV | Annually | 2022-06-01
| Record UV lamp hours. Check UV dose is within range. If not arrange for service. | UV | Monthly | 4000 hrs
| Duty UVI sensors must be checked at least monthly against the reference sensor. If the difference between the two readings exceeds the manufacturer’s specified limits, then the Duty UVI sensor must be replaced. | UV | Monthly | Checked
| Standardise UVI sensor (Date last done) | UV | Annually | 2022-06-01
| Follow water storage management plan, including the following: Check lids are secure. Check tank openings (inlets, overflows, gaps) are all closed or screened to prevent access by vermin, birds and other sources of contamination. | Water tanks | 3 Monthly | Checked
| Test all testable backflow prevention devices installed. Keep a register of the location of all point of supply testable backflow protection devices, device types, assessed risk level and the results of testing of all devices. | Distribution | Annually | 2022-06-01
| Test all testable backflow prevention devices (date and result of last test) | Distribution end point | Annually | Passed 12/08/2022
| Clean first flush diverters. | First flush diverter | Monthly | Done
| Drain and clean tank out. | Raw water tank (roof supplies) | 5-yearly | 2019-09-07
| Check chemical stock levels and re-stock if required. Maintain as per manufacturer's requirements. | Chlorination | Monthly | 2022-06-01
Monitoring | E. coli (MPN/100 mL) | All sources | 2 per Month | 100
| Total Coliforms (MPN/100 mL) | All sources | 2 per Month | 200
| Iron (mg/L) | All sources | Monthly | 0.02
| Manganese (mg/L) | All sources | Monthly | 0.001
| Colour (TCU) | All sources | Monthly | 3
| Nitrate (mg/L) | All sources | Monthly | 0.2
| Conductivity (µs/cm) | All sources | Monthly | 100
| pH | All sources | Monthly | 7.2
| Turbidity (NTU) | All sources | Monthly | 2
| Alkalinity, antimony, arsenic, barium, cadmium, calcium, chloride, chromium, copper, lead, magnesium, mercury, nickel, sodium and sulphate monitoring (Date last done). | All sources | Annually | 2022-06-01
| Gross alpha activity, gross beta activity and potassium monitoring (Date last done) | Bore | 10 Yearly | 2020-06-01
| Cadmium, copper, zinc, lead, benzo[a]pyrene (In winter – June, July, or August) monitoring (Date last done) | Roof source | 3 Yearly | 2022-06-01
| E. coli (MPN/100 mL) | Treated water | Monthly | <1
| Total Coliforms (MPN/100 mL) | Treated water | Monthly | <1
| Any chemical used in the treatment process (excluding FAC) | Treated water | Monthly | Alum: 0.1 mg/L
| Chlorate (if sodium hypochlorite is used) | Treated water | 3 Monthly
| E. coli | Distribution end point | Monthly | <1
| Total Coliforms | Distribution end point | Monthly | <1
| FAC (mg/L) | Distribution end point (networked supply) | 3 per week | 0.3
| Antimony, cadmium, chromium, copper, lead, mercury, nickel, zinc (Date last done) | Distribution end point (networked supply) | Annually | 2022-06-01
| Disinfection by-products: chloroform, bromodichloromethane, dibromochlorormethane, dichloracetic acid, trichloracetic acid | Distribution end point (networked supply) | 1 per quarter | 2022-06-01
Continuous monitoring | Turbidity (NTU) | Treated water | Continuous
| UVI or UV dose (at the reactor) | Treated water | Continuous
| Flow | Treated water | Continuous
| pH | Treated water | Continuous
| Differential pressure across cartridge filters | Treated water | Continuous
| Cartridge filter service state (each filter) | Treated water | Continuous
Note on D40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Can reduce to 6-monthly if no significant variation in the first 12 months of samples. Continuous sampling is required if the source is a bore which is Class 2, 3 or 4.
Note on D41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Can reduce to 6-monthly if no significant variation in the first 12 months of samples. Continuous sampling is required if the source is a bore which is Class 2, 3 or 4.
Note on D42: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Can reduce to 6-monthly if no significant variation in the first 12 months of samples. Continuous sampling is required if the source is a bore which is Class 2, 3 or 4.
This shape represents a table slicer. Table slicers are not supported in this version of Excel. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.

## Guidelines
Drinking Water Maintenance and Servicing Guidelines
Where does contamination come from?
There are two main sources of contamination: microbial and chemical. Microbial contamination includes: - Feaces from birds, animals and insects - Decaying organic matter - Contaminants from surface and groundwater e.g. soil organisms Chemical contamination includes: - dissoved contaminants in the source water - spray drift from chemical applications e.g. pesticides - paint or roof coatings - roofing materials such as lead - emissions from flues and chimneys - emissions from vehicles and industrial processes
Note: Contaminants can accumulate in tanks such that the concentrations of chemicals can become very high
How do we prevent or limit contamination and ensure water supply is reliable?
Roof Catchment 1. Ensure the roof catchment is in good condition and made from stable and safe materials e.g. well painted steel. 2. Regularly clean the roof and remove debris. 3. Keep the roof catchment clear of overhanging branches to limit pests and organic material getting on the roof. 4. Avoid installing a TV aerial or other fixture on the roof which encourages birds to roost. 5. Install mesh leaf guards on gutters and leaf screens to downpipes to keep debris out of tanks. 6. Install a first flush diverter to direct the first flush of water (which contains most of the contaminants) away from the storage tank. 7. Install downpipe diverters. If maintenance is being undertaken on the roof or if significant spray drift is anticipated, disconnect pipes from the tank and only reconnect after the roof has been washed by rain.
Groundwater Bore 1. Ensure the bore is fenced or contained so that animals cannot approach the bore within 5 m. 2. Ensure the borehead is sealed preferably with a concrete pad extending 1 m in every direction so that any stormwater is shed away from the bore. 3. Ensure any bore pump is regularly serviced based on the manufacturer's recommendation for run hours. 4. Undertake comprehensive testing of the bore water quality at least every 3 years.
Storage Tanks 1. Install a calmed inlet to reduce sediment disturbance during tank filling 2. Install a floating intake to ensure water is drawn from the surface where it is cleanest 3. Ensure all access covers are tight and secure from unauthorised access 4. Ensure any penetrations and gaps are fitted with insect proof mesh (1.5 mm gap) to prevent vermin, insect or debris entry 5. Fit flap valves to the open ends of overflow pipes to keep vermin and insects out 6. For below ground storage tanks, ensure surface water runoff and groundwater cannot get into the tank 7. Ensure any leaks and cracks in the tanks are either repaired, or if not repairable, replace the tank
Treatment Plant 1. Ensure the filter cartridge(s) are replaced at the manufacturer's recommended frequency or when pressure monitoring or water quality indicates they should be replaced. 2. Ensure the UV lamp is replaced at the manufacturer's recommended frequency but at least annually. 3. Ensure any consumables for softening or ion exchange filters are topped up as required. 4. Ensure any disinfection equipment is serviced at the recommended internval and at least once per year. 5. Ensure all other components of the treatment plant such as meters, monitors and gauges are checked and serviced at least once every year.
Distribution System 1. Ensure any leaks in the network are fixed promptly. 2. Assess the distribution system for backflow risks once a year. A backflow prevention device or air gap must be installed if there is a risk of backflow, to prevent the drinking water supply from becoming contaminated. 3. Ensure any backflow devices are checked and tested at least once every year. Argest will organise this once the device is on its backflow register. 4. Ensure any distribution pumps are checked and serviced based on manufacturer's recommended frequency for run hours.