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[bookmark: _Toc240467924]School Details
[bookmark: _Toc240467925]Background and Population
[bookmark: _Toc240467967]Table 1‑1: School background, population and building information
	School name
	

	Number of people served by the water supply
	Students and Staff (current) – 
Students and Staff (future – 2033) – 
Houses – 
Other – 
Total (P) – 

	Peak population (e.g. during events)
	

	Number of buildings supplied with drinking water
	

	Other components supplied with drinking water (e.g. pool, irrigation)
	

	Address
	

	Hinekōrako Code
	

	Compliance pathway
	





[bookmark: _Toc240467926]Key Contacts
	Role and organisation
	Name
	Contact details

	Caretaker
	
	Email:
Phone: 
Mobile: 

	Plumber
	
	Email:
Phone: 
Mobile:

	Maintenance Contractor
	
	Email:
Phone: 
Mobile:

	Consumables supplier (e.g. cartridge filter, UV lamp)
	
	Email:
Phone: 
Mobile:

	Registered Water Carrier
	
	Email:
Phone: 
Mobile:

	New Zealand School Property Agency
	Water Services Team
	Email: water.services@schoolproperty.govt.nz





[bookmark: _Toc240467927]Description of Water Supply
[bookmark: _Toc240467928]Source
The school sources its water from a rainwater supply and from a groundwater supply. A groundwater supply can be either a bore or a spring supply. The details of the supply are summarised in Table 2-1 and Table 2-2.
[bookmark: _Toc240467968]Table 2‑1: Details of the rainwater supply
	Water source
	Roof

	What is the total roof area used to collect drinking water (in m2)?
	

	Is the roof material suitable for drinking water?
	

	What is the condition of each of the roofs used to collect drinking water?
	

	What measures does the school already have in place to reduce contaminants from the roof entering the water supply?
	


[bookmark: _Toc240467969]Table 2‑2: Details of the groundwater supply
	Water source
	Bore

	Well number
	

	Property owner of land on which the bore is located
	

	Bore depth (m)
	

	Casing diameter (m)
	

	Drilling date
	

	Screen present?
	

	Is the bore pump located down the bore or above ground?
	

	Groundwater source and headworks protection
	Copy the applicable protection measures the school already has in place from the guidance document.

	Photo of bore headworks
	



	Water source
	Spring

	Property owner of land on which the spring is located
	

	Groundwater source and headworks protection
	Copy the applicable protection measures the school already has in place from the guidance document.

	Photo of spring headworks
	


[bookmark: _Toc240467929]Treatment
The school water treatment plant consists of the following components:
Pretreatment 
Cartridge filtration
UV disinfection
Residual chlorination
Details about each of the main treatment components and the treatment plant housing can be found in the tables below.
[bookmark: _Toc240467970]Table 2‑3: Details of the cartridge filtration system
	Number of cartridge filters
	

	What is the pore size on each cartridge filter?
	

	How often are the cartridge filters replaced?
	

	Is differential pressure measured across each filter?
	

	Photo of cartridge filters
	

[bookmark: _Toc240467971]Table 2‑4: Details of the UV disinfection system
	UV unit make and model
	

	Is the UV unit validated for NSF/ANSI 55 for class A systems?
	

	Does flow through the UV unit stop automatically on low UV intensity (UVI) or low dose (e.g., via a solenoid valve)?
	

	Is there a lamp status indication?
	

	Is there an alarm? If yes, is it an audible or visual alarm?
	

	How often is the UV unit serviced?
	

	Photo of UV system
	

[bookmark: _Toc240467972]Table 2‑5: Details of pretreatment process
	Pretreatment type
	

	Pretreatment process details
	

	Photo of pretreatment process
	[image: ]


[bookmark: _Toc240467973]Table 2‑6: Details of pH correction
	Method of pH correction (e.g. acid dosing, calcium carbonate)
	

	Photo of pH correction system
	


[bookmark: _Toc240467974]Table 2‑7: Details of the chlorination system for residual disinfection
	Chlorine type
	Hypochlorite

	What is the target chlorine concentration for water leaving the treatment plant (mg/L)?
	

	What is the target chlorine concentration for water in the distribution system (mg/L)?
	

	Photo of chlorination system
	[image: ]EXAMPLE



[bookmark: _Toc240467975]Table 2‑8: Water treatment plant housing details
	Treatment plant housing (e.g., locked shed)
	

	Photo of treatment plant housing exterior
	[image: ]EXAMPLE    


	Photo of treatment plant housing
	[image: ]EXAMPLE    



[bookmark: _Toc240467930]Storage
[bookmark: _Toc240467931]2.3.1.	Untreated Water Storage
The school has a total of XX L untreated water storage. To prevent contamination of the untreated water, it is important that the tanks are in average or good condition, have vermin protection in place and have secure lids. Details of the untreated storage tank(s) are provided in the table(s) below. 
[bookmark: _Toc240467976]Table 2‑9: Untreated water storage tank details
	Tank number
	

	Volume (L)
	

	Material
	

	Condition
	

	Year installed
	

	Vermin protection
	

	Photo of tank
	

[bookmark: _Toc240467932]2.3.2.	Treated Water Storage
The school has a total of XX L treated water storage. To prevent contamination of the treated water, it is important that the tanks are in average or good condition, have vermin protection in place and have secure lids. Details of the treated storage tank(s) are provided in the table(s) below.
[bookmark: _Toc240467977]Table 2‑10: Treated water storage tank details
	Tank number
	

	Volume (L)
	

	Material
	

	Condition
	

	Year installed
	

	Vermin protection
	

	Photo of tank
	

[bookmark: _Toc240467933]Distribution System
[bookmark: _Toc240467934]2.4.1.	Backflow Prevention 
Backflow into the drinking water supply can present a risk if contaminated water enters the treated water distribution system. This can affect both the quality and safety of the water supply[footnoteRef:2].  [2:  NZ Building Code Acceptable Solutions and Verification Methods – Clause G12 Water Supplies] 

All hose taps in the school do / do not have a permanently attached hose connection vacuum breaker.
The medium or high hazard backflow activities connected to the drinking water supply that require a backflow prevention device are captured in the table below. 
[bookmark: _Toc240467978]Table 2‑11: Medium or high hazard backflow activities connected to the school's treated water supply
	Activity
	Hazard
	Type of backflow prevention device required
	Type of backflow prevention device installed
	Listed on Argest register[footnoteRef:3] [3:  Argest undertakes annual testing of all testable backflow prevention devices on its register.] 

	Meets requirements?

	
	
	
	
	
	

	
	
	
	
	
	





[bookmark: _Toc240467935]Aerial View and Schematic of Water Supply
An aerial image of the school showing key features of the water supply, and a schematic showing the details of the water supply, are shown in the figures below. Replace this aerial image with an aerial image which is labelled to show the school and its key supply components


[bookmark: _Toc240467986]Figure 2‑1: Water supply roof catchments, bore, treatment and storage locations
[image: ]
[bookmark: _Toc240467987]Figure 2‑2: School water supply and treatment schematic
[bookmark: _Toc240467936]Daily Water Demand and Storage Requirements
The estimated average daily water demand is captured in the table below.
[bookmark: _Toc240467979]Table 2‑12: Daily water demand
	Water users
	Average daily water use (litres per day)

	Staff and students
	

	Pool
	

	Houses
	

	Community hall
	

	Early childhood centres
	

	Other (describe)
	

	Total estimated daily demand (Q)
	


[bookmark: _Toc240467937]2.6.1.	Untreated Water Storage
The New Zealand School Property Agency recommends that self-supplying schools relying on groundwater store enough untreated water to meet the school’s demand of at least 7 days. More storage volume will be required for schools if there has been a problem in the past with the school running out of water. If this is the case, please contact the Water Services team at NZSPA for a roof water storage assessment. 
The volume of untreated drinking water storage required (VU) is the estimated daily demand (Q) multiplied by the number of days untreated water storage is required for (RU). This is captured in the table below.
[bookmark: _Toc240467980]Table 2‑13: Untreated water storage requirements
	Requirement for untreated water storage for rainwater supplied schools (RU)
	7 days

	Minimum volume untreated drinking water required (VU)
	XX litres

	Volume of untreated water storage capacity currently available
	XX litres


There is enough untreated water to meet the New Zealand School Property Agency’s requirements / To meet the New Zealand School Property Agency’s requirements, an additional XXX L of untreated water storage needs to be installed. 
[bookmark: _Toc240467938]2.6.2.	Treated Water Storage
NZSPA recommends that self-supplying schools store enough treated drinking water for three days, both to minimise disruption if there is a treatment plant outage and to provide enough during an emergency. The volume of treated drinking water storage required (VT) is the estimated daily demand (Q) multiplied by the number of days treated water storage is required for (RT). This is captured in the table below.
	Requirement for treated water storage (RT)
	3 days

	Minimum treated drinking water required (VT = Q x RT)
	XX litres

	Treated water tank size required (VT)
	XX litres

	Volume of treated water storage capacity currently available
	XX litres


There is enough treated water to meet the New Zealand School Property Agency’s requirements / To meet the New Zealand School Property Agency’s requirements, an additional XXX L of treated water storage needs to be installed.
[bookmark: _Toc240467939]Resource Consent
The groundwater take does not require a resource consent.
The school has a resource consent for the groundwater take and the consent number is XX.
The groundwater take requires a resource consent, but the school does not have a consent. Applying for a consent has been added to the improvement plan in section 4.2.
[bookmark: _Toc240467940]Te Mana O Te Wai
The National Policy Statement for Freshwater Management is that freshwater is managed in a way that gives effect to Te Mana o te Wai. Te Mana o te Wai recognises that protecting the health of freshwater protects the health and well-being of the wider environment. It sets the following hierarchy of obligations: 
‘First, the health and well-being of water bodies and freshwater ecosystems; and
Second, the health needs of people (such as drinking water); and
Third, the ability of people and communities to provide for their social, economic, and cultural well-being, now and in the future.’ 
The school gives effect to Te Mana o Te Wai in the following ways:
Copy applicable ways in which the school gives effect to Te Mana o Te Wai from the guidance document
The school plans to improve the way it gives effect to Te Mana o Te Wai in the following ways:
Copy applicable improvements from the guidance document


[bookmark: _Toc240467941]Source Water Risk Management Plan
[bookmark: _Toc240467942]Catchment Description
The school is in the XX region. The catchment for the drinking water supply includes the roofs on the following buildings: 
List buildings used for collecting roof water 
Although the catchment for the drinking water supply includes the catchment of the aquifer that may feed the spring and/or bore, this Source Water Risk Management Plan (SWRMP) only considers the area around the groundwater take up to 2.5 km from the bore/spring. 
Figure 3-1 shows the location of the groundwater take in relation to the surrounding area.Replace this aerial image with an aerial image which shows the groundwater take in relation to the surrounding area


 Figure 3-1: Aerial image showing the location of the groundwater take 
[bookmark: _Toc240467943]Impact of Catchment Activities on Water Quality
[bookmark: _Toc240467944]3.2.1.	Impact of Catchment Activities on Roof Water Quality
Given that the school’s drinking water is partly supplied by rainwater, the following activities may impact the roof water quality:
Faecal matter from birds and other animals on the roof 
Copy applicable contaminant sources from the guidance document
The school plans to improve the quality of the roof water collected as follows:
Copy applicable improvements from the guidance document
[bookmark: _Toc240467945]3.2.2.	Impact of Catchment Activities on Groundwater Quality
Given that the school’s drinking water is partly supplied by groundwater, the following activities may impact the groundwater quality: 
Copy applicable contaminant sources from the guidance document
The school plans to reduce the contamination risk in the area around the groundwater take as follows: 
Copy applicable improvements from the guidance document
[bookmark: _Toc240467946]Water Quantity Available From Source
[bookmark: _Toc240467981]Table 3‑1: Previous water quantity issues
	Has there been a problem with lack of water over the past ten years?
	

	If yes, provide details:
	

	If yes, have there been any improvements to address these or are there any planned?
	


[bookmark: _Toc240467947]Climate Change Impacts
Climate related factors influencing catchment conditions and water demand include rainfall and temperature. With climate change, rainfall patterns are expected to become more variable and total annual rainfall will drop in some areas (particularly the east coast and the north of the North Island), which will mean that roof water will become a less reliable source. Groundwater sources may also be impacted. In addition, increasing temperatures may lead to an increased demand on the water supply, particularly if it is used for outdoor uses such as irrigation and/or a swimming pool. In the future, the school may need to increase the roof area used for collecting roof water, increase the storage volume and/or find an alternative source, to continue to provide a reliable water supply.
[bookmark: _Toc240467948]Cyanobacteria 
Given that the school is supplied by roof water and groundwater, it is categorised as a low risk for the presence of cyanobacteria. 


[bookmark: _Toc240467949]Risks and Improvement Actions
[bookmark: _Toc240467950]Risk Assessment
Table 4-1 summarises the key risks for the drinking water supply, both in terms of safety and having enough water. It describes:
What could cause these risks to happen.
The ways these events could be identified.
The existing preventive measures in place to reduce the likelihood of the event happening or the consequence if it did occur.
The residual risk rating once the existing preventive measures are considered. The following risk definitions have been used:
Low: Insignificant or minor consequence, with little disruption to normal operation; not likely to happen.
Medium: Significant manageable disruption to safe water supply, with requirement for increased monitoring. Potential aesthetic issues; likelihood possible.
High: Major disruption to safe water supply, e.g., complete failure of systems, acute harm to people or widespread illness; high level of monitoring and incident management required; likely to happen.
The additional improvements that are needed to reduce the risk to an acceptable level.


	
	
	



	
	
	




	
	
	



[bookmark: _Toc240467982]Table 4‑1: Risks and improvement actions
	Supply Component
	Event Description
	Possible Causes
	Existing Measures to Identify the Hazard
	Existing Preventive Measures
	Residual Risk
	Improvement

	Source Water
	Contamination of source water by faecal material.
	Source water receives faecal matter from animals on the catchment area.
Wastewater disposal field located close to the groundwater source. 
	E. coli or total coliforms measured in raw water samples. 
Visual evidence of animals on the catchment area.
	Leaf screens on all supply downpipes
Leaf screens on some supply downpipes
First flush diverter(s) for some of the roof water entering the untreated water storage tanks  
First flush diverter(s) for all of the roof water entering the untreated water storage tanks  
Bore has sanitary borehead above ground level
Livestock cannot get within 5 metres of the bore 
Wastewater effluent disposal field is at least 20 metres from the bore 
Cartridge filtration
UV disinfection
	Low
Medium
High
	Install leaf screens on all supply downpipes
Install first flush diverter(s) for all roof water entering the untreated water storage tanks  
Install sanitary borehead
Fencing an area at least 5 metres around the bore headworks 
Consider relocating bore or effluent disposal field to increase separation
Install cartridge filtration
Install UV disinfection

	Source Water
	Contamination of source water by chemicals
	Nearby spraying
Unsuitable roof materials
Solid fuel heaters and/or boilers on site.
Contaminated site
Landfill
Pesticides applied to land
Geothermal or geological influences
Metal pipe and fittings
	Observed use of agricultural or horticultural spraying near the school.
Taste or odour complaints
Source water chemical testing.
	First flush diverter(s) for some of the roof water entering the untreated water storage tanks  
First flush diverter(s) for all of the roof water entering the untreated water storage tanks 
Roof materials are suitable for contact with drinking water
Solid fuel heaters and boilers aren’t used on site
Bore has sanitary borehead above ground level
Abstraction depths over 30 metres below ground level with confining layers
No known potentially contaminating activities within 2.5 km of the bore/spring
	Low
Medium
High
	Install first flush diverter(s) for all roof water entering the untreated water storage tanks  
Monitor chemicals in line with the Quality Assurance Rules / Acceptable Solution
Perform regular inspections of the roof source to identify maintenance requirements and deterioration
Ask neighbouring farmers to notify the school before they spray. Before spraying starts, disconnect the roof water collection system and reconnect once it has been washed clean (e.g. by the rain)
Replace roof materials with materials that are suitable for contact with drinking water
Decommission solid fuel heaters/boilers
Install sanitary borehead above ground level
Monitor chemicals in line with the Quality Assurance Rules 
Perform regular inspections of the headworks to identify maintenance requirements and potential contamination 
Investigate alternative water source

	Source Water
	Insufficient source water
	Periods of little to no rainfall
Insufficient storage volume
Leakage from untreated water storage tanks
Pump failure
Water abstraction /pumping exceeds recharge rates
Insufficient storage volume
	Local reports of drought.
Low levels in untreated water tank.
Bore runs dry.
	No historical issues with running out of source water 
The school has 7 days of untreated water storage
Tanker supply from a registered water carrier
	Low
Medium
High
	Install tanks to provide 7 days of untreated water storage
Investigate alternative water source 
Residual risk may increase in future due to climate variability. Consider proactive measures such as increasing storage or alternative sources.

	Storage
	Contamination of supply
	Animals, birds, or insects entering water storage tanks. 
Vandalism
Contamination enters though unsealed / unmeshed gaps 
Rainwater enters through gaps or cracks in the tank
	E. coli or total coliforms measured in the distribution system.
Visual sign of entry point for animals, birds, or insects during routine inspection.
Visual signs of cracking or damage to the roof during routine inspection.
Complaints about taste or odour.
Visual signs of vandalism during routine inspection.
	All tanks are in average, good or very good condition
All tanks are secure from access by animals, birds and insects, with all penetrations sealed and all openings covered by insect mesh or a flap valve.
Measures are in place to prevent vandalism 
Regular visual checks carried out to identify any locations where water from the roof may enter or any vandalism.
	Low
Medium
High
	Replace all poor and very poor condition tanks
Repair tanks so that there are no ingress points for vermin or insects
Schedule regular inspections of the tanks
Install measures to prevent vandalism

	Treatment – Pre-treatment
	Chemical or physical contaminants are not controlled to acceptable level
	Inadequate treatment process 
Inadequate filter maintenance
Failure to replenish reagents
	Caretaker check of local display of reagent levels and unit operation
Taste or odour issues in treated water
Treated water chemical testing
	Weekly checks of pre‑treatment system and reagent levels 
The pre-treatment system is serviced every 6 months
	Low
Medium
High
	Schedule weekly checks of pre‑treatment system and reagent levels 
Schedule servicing of the pre-treatment system every 6 months
Quarterly testing of chemical constituents exceeding 50% of MAV

	Treatment – Cartridge Filtration
	Particles and/or natural organic matter (e.g. from leaves) not removed
	Inadequate filter maintenance.
Using incorrect filters or missing filters
	Elevated turbidity in filtered water.
E. coli or total coliforms detected in treated water.
	There is cartridge filtration, including a filter with a pore size of 5 microns or smaller 
The filters are replaced every 6 months or earlier as required
Cartridge filters cannot be bypassed
	Low
Medium
High
	Install cartridge filtration
Schedule cartridge filter replacement as per manufacturer’s recommendations
Remove bypass

	Treatment – UV Disinfection 
	Inadequate disinfection
	Inadequate UV intensity or dose.
Power outage leading to no UV disinfection.
Using incorrect UV lamps.
	E. coli or total coliforms detected in treated water.
Alarm active on UV control unit indicating power failure, lamp failure and/or low UV dose.
Low UV transmissivity due to no or inadequate pre-treatment
Scale formation on the UV sleeve(s) (e.g. from high levels of calcium in the water).
Absence of maintenance records.
Repeated power failures of a duration that threatens the ability to supply treated water to consumers.
	Annual UV servicing, including cleaning sleeves and replacing lamps
Person responsible for maintaining the drinking water supply is trained in the maintenance schedule of the UV units and undertakes maintenance in accordance with the schedule
Solenoid valve automatically stops flow through the UV unit if there is a UV fault
UV unit cannot be bypassed
	Low
Medium
High
	Schedule UV servicing as per manufacturer’s recommendations.
Ensure the person responsible for maintaining the drinking water supply is trained in the maintenance schedule of the UV units and undertakes maintenance in accordance with the schedule
Install a solenoid valve to automatically stop flow through the UV unit if there is a UV fault
Remove bypass

	Treatment – Residual Chlorination
	Low chlorine residual in the treated water 
	High chlorine demand (e.g. from high organic load).
Chlorine chemical supply is exhausted.
Problems with the chlorine dosing pump.
Hypochlorite is past its expiry date.
Contaminants entering the water supply network via backflow or leaks.
	E. coli or total coliforms measured in the treated water at the tap.
Reports of illness within the community that may be linked to water quality.
Supply of hypochlorite found to be exhausted during routine site visits.
Low level chlorine alarm.
Free available chlorine (FAC) is less than 0.5 mg/L as it leaves the treatment plant or less than 0.2 mg/L in the distribution system (i.e., at a drinking water tap).
	FAC is monitored regularly with a handheld meter or continuous analyser
Annual maintenance of the chlorination system
Hypochlorite is replaced at least every 3 months
Person responsible for maintaining the drinking water supply is trained in the maintenance schedule of the chlorination plant and undertakes maintenance in accordance with this
	Low
Medium
High
	Purchase a handheld FAC meter and monitor FAC concentration in accordance with the Drinking Water Quality Assurance Rules
Schedule regular maintenance of the chlorine dosing system 
Schedule regular replacement of hypochlorite (every 3 months)

	Treated Water
	Loss of supply
Inadequate treated water
	Not enough water in treated water tanks to meet demand due to poor performance or failure of the water treatment plant.
Pump failure.
Leakage from treated water tanks.
	Low pressure or no water.
Visual sign of leakage from tanks upon inspection.
Reduction in water storage levels.
	Weekly inspection of treatment plant and tank levels. 
All tanks are in excellent, good or average condition.
Treated water storage tank which holds 3 days of treated water
	Low
Medium
High
	Replace tanks that are in poor condition.
Install smart flow meter and monitor water usage.
Install remote monitoring of alarms and storage volume.
Install a treated water storage tank which holds 3 days of treated water

	Distribution
	Loss of supply

Extraordinary water use
	Leakage.
Excessive usage.
Demand exceeds supply from the water treatment plant.
	Loss of pressure in areas of the network.
Observation of water leaks or wastage in the distribution network.
Pressure complaints from consumers.
Water quality complaints.
	No problems with a lack of treated water
No problems with low pressure
No obvious leaks and all leaks are fixed promptly
Water efficient devices are installed
Treated water storage tank which holds 3 days of treated water
	Low
Medium
High
	Install a treated water storage tank which holds 3 days of treated water
Fix leaks 
Install water efficient devices 
Install a smart water meter and monitor water usage.

	Distribution
	Loss of power means the treatment plant and pumps cannot operate
	Power outage
	Power outage
Water supply stops
	Power outages are rare
Portable generator 
	Low
Medium
	Purchase a portable generator to power the distribution pump

	Distribution
	Contamination of supply
	Backflow of water from the hazardous activity back into the distribution system
Cross-connection between potable and non-potable supply
Poor condition pipes allow contaminants to enter the distribution network
	Illness or injury (e.g. to skin).
Water quality complaints.
E. coli or total coliforms detected in the distribution system.
	There are no activities which are a high or medium backflow hazard connected to the treated water supply
Backflow prevention device is installed
Permanently attached vacuum breakers are installed on all hose taps
There are no cross-connections between the potable and non-potable supplies (or there is no non-potable supply)
Distribution pipework is in good condition
	Low
Medium
High

	Install a backflow prevention device on the supply to all high and medium risk activities
Install permanently attached vacuum breakers on all hose taps
Remove all cross-connections between the potable and non-potable supplies
Replace distribution pipework


	
	
	



	
	
	




	
	
	



[bookmark: _Toc240467951][bookmark: _Hlk170328346]Improvement Actions
The improvement actions identified in the previous sections of the report and the risks and improvement actions table are summarised in Table 4-2. The improvements have been prioritised as follows:
Urgent improvements are those which address drinking water safety concerns or address a lack of water (i.e. high risk).
Non-urgent improvements are those which improve the resilience and reliability of the supply, or enable full compliance with the Drinking Water Quality Assurance Rules/Acceptable Solution.
[bookmark: _Toc240467983]Table 4‑2: Summary of improvement measures the school will take to minimise risks
	Supply Component
	Improvement
	Priority

	Source Water
	
	Urgent
Non-urgent

	Treatment
	
	Urgent
Non-urgent

	Storage
	
	Urgent
Non-urgent

	Distribution
	
	Urgent
Non-urgent





[bookmark: _Toc240467952]Operations, Maintenance, Monitoring and Reporting
[bookmark: _Toc240467953]Operations and Maintenance Activities 
The maintenance and servicing requirements of the school, as per the “Maintenance and Servicing Guideline and Checklist” tool have been compiled in Appendix A. 
The operation and maintenance manual that covers the day-to-day operations of the water supply system is stored in XXX. 
[bookmark: _Toc240467954]Previous Water Quality Issues
[bookmark: _Toc240467984]Table 5‑1: Previous water quality issues
	Has E. coli been detected in the treated water over the past five years?
	

	If yes, provide details:
	

	If yes, have there been any improvements to address these or are there any planned?
	


[bookmark: _Toc240467955]Monitoring and Reporting 
The water quality monitoring requirements for the water supply can be found in the “Maintenance and Servicing Guideline and Checklist” tool. The New Zealand School Property Agency is in discussion with the Water Services Authority Taumata Arowai to develop a practical approach to monitoring. In the meantime, the school should sample and test for E. coli and total coliforms in the treated water at the tap monthly, as well as periodic source water testing as recommended by NZSPA. Additional monitoring will be required for any other parameters which exceed 50% of the MAV in the source water.
Since the school is using an Acceptable Solution, no reporting is required to the Water Services Authority Taumata Arowai.
Since the school is a small supply under the Drinking Water Quality Assurance Rules, 6-monthly reporting to the Water Services Authority Taumata Arowai is required.
Since the school is a medium supply under the Drinking Water Quality Assurance Rules, 3-monthly reporting to the Water Services Authority Taumata Arowai is required.
Since the school is a large supply under the Drinking Water Quality Assurance Rules, monthly reporting to the Water Services Authority Taumata Arowai is required.
The New Zealand School Property Agency is in discussion with the Water Services Authority Taumata Arowai to develop a practical approach to reporting. In the meantime, the school should capture its monitoring results in the monitoring spreadsheet in the “Maintenance and Servicing Guideline and Checklist” tool, so that they can provide this information at a future date.
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The contingency plans in Table 6-1 have been developed to guide the school about the action required following a serious event. If there is uncertainty around how serious an event is, contact the Water Services Authority Taumata Arowai.  
The school must notify Taumata Arowai and NZSPA (water services/property advisor) of any event where:
The drinking water is or may be unsafe.
The drinking water does not comply with the drinking water standards.
Enough drinking water can’t be provided.
There is a ‘notifiable risk or hazard’ (declared by Taumata Arowai).
[bookmark: _Toc240467985]Table 6‑1: Contingency plans for the school water supply
	Event
	Indicators
	Required Action

	Water Contamination
Examples:
Severe microbiological contamination of the abstracted source water (such that treatment is ineffective).
Roof contaminated by spray drift or over spraying (chemical contamination)

	A contamination event in the catchment area may be observed by or reported to the school. 
E. coli (greater than 0 per 100mL) or total coliforms (greater than 10 cfu/mL) detected in water that has been treated, indicating bacterial contamination.
Complaints of discoloured, strange tasting or smelling water coming from taps, indicating chemical contamination.
Treatment plant failure (e.g., UV dose too low)
Roof water source: Spray drift or over spraying reported indicating possible chemical contamination.
Reports of illness within the community that may be linked to water quality.
	Notify NZSPA (water services and property advisor) and determine if the Water Services Authority Taumata Arowai and/or the Medical Officer of Health needs to be notified.
Investigate the cause and inspect source and treatment plant to rectify the problem as quickly as possible.
Provide another source of drinking water until water of acceptable quality can be supplied again (e.g., bottled water, tanker water)
Record incident and actions taken.
In a case of bacterial contamination:
Implement ‘boil water’ notice (see Appendix C).
Commence daily E. coli sampling at the post-treatment and distribution zone sampling points, until three consecutive samples are <1 per 100 mL.
Consider increased disinfection using chlorine and flushing the network.
Disable drinking water fountains.
In a case of chemical contamination:
Implement ‘do not drink’ notice.
Flush distribution system (or isolated area of distribution system if the problem is isolated to that area). 
For roof spray contamination: Identify the person or organisation doing the spraying, and if possible, the product used. Drain the contents of the tank(s) connected to the roof. Disconnect the downpipe from the tank. Clean roof and tank. Reconnect the downpipe to the tank. 
Monitor appropriate determinands in the affected area to assess the effectiveness of the contingency measures.
Notify customers, when the supply is safe to use, that they need to flush their taps before use.
Update the Drinking Water Safety Plan if necessary.

	Water Shortage
	Reduced or no flow reaching the treatment plant.
Unexpectedly high water usage 
Leaks in the system
	Notify the principal and determine if the Water Services Authority Taumata Arowai needs to be notified.
Organise alternative water source (e.g., tanker water)
Determine if the alternative water supply is sufficiently different in water quality to impact on effective treatment e.g. disinfection.
Consider restricting water use.
Implementation of a permanent alternative water source may need to be considered if water shortages occur frequently because result of low water availability.
Record incident and actions taken.
Determine cause of shortage (drought/leakage)
Check for supply leakage and make necessary repairs before reinstatement
Update the Drinking Water Safety Plan if necessary

	Natural Disaster
	Personal experience of the event and/or local reports from the area or region.
Media coverage of activity.
	In the event of a significant natural disaster, the immediate response to the event and potential school closure will be managed by the principal in conjunction with Civil Defence. 
Once access to the water treatment plant has been obtained:
Full checks of all the plant and equipment to establish it can be operated.
Visual checks of all water storage tanks to check for damage and verify water tightness.
Check the turbidity of the source and filtered water to determine if the turbidity has increased.
If the effectiveness of the treatment process (due to potential damage) has been impacted, put measures in place to assure the supply of safe drinking water.
Monitor leaks in the network and repair them.
Record incident and actions taken.
Update the Drinking Water Safety Plan if necessary.





[bookmark: _Toc240467957]Review
Each year on its anniversary date and any time there are material changes in the water supply or contact information, this plan is to be reviewed, updated, and approved by the Board of Trustees to check that it is meeting its purpose. This is done by:
Checking compliance with the Drinking Water Quality Assurance Rules in the monitoring report to the Water Services Authority Taumata Arowai.
Checking compliance with the Acceptable Solution
Checking to see if any issues have been identified as part of the routine maintenance checks.
Reviewing the response to adverse events (e.g. E. coli contamination or loss of water supply).
If there has been a non-compliance or issue identified, the drinking water safety plan is to be updated to include:
Any new risks or causes identified (e.g., change to the monitoring events/equipment failure, changes in operating staff, changes in the source. 
Any new preventative measures (for both existing and new causes) 
The improvement schedule should be updated to include the most up-to-date information. Such updates could include:
Additional improvements planned for the school.
Improvements that have been completed.
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[bookmark: _Toc240467959]Taumata Arowai
Drinking Water Standards, Drinking Water Quality Assurance Rules and Drinking Water Aesthetic Values: https://www.taumataarowai.govt.nz/drinking-water-suppliers-and-operators/for-drinking-water-suppliers/ways-to-comply/drinking-water-quality-assurance-rules
 Drinking Water Acceptable Solutions: https://www.taumataarowai.govt.nz/drinking-water-suppliers-and-operators/for-drinking-water-suppliers/ways-to-comply/acceptable-solutions 
Taumata Arowai homepage: https://www.taumataarowai.govt.nz/
 Notify Taumata Arowai: https://www.taumataarowai.govt.nz/drinking-water-suppliers-and-operators/notify-us
Registered water carriers: https://www.taumataarowai.govt.nz/for-the-public/public-registers#e697
[bookmark: _Toc240467960]Legislation and Regulations
Water Services Act 2021: https://www.legislation.govt.nz/act/public/2021/0036/latest/LMS374564.html
Water Services (Drinking Water Standards for New Zealand) Regulations 2022: https://www.legislation.govt.nz/regulation/public/2022/0168/latest/whole.html
NZ Building Code Acceptable Solutions and Verification Methods – Clause G12 Water Supplies: https://www.building.govt.nz/building-code-compliance/g-services-and-facilities/g12-water-supplies/
National Policy Statement for Freshwater Management: https://environment.govt.nz/acts-and-regulations/national-policy-statements/national-policy-statement-freshwater-management/
[bookmark: _Toc240467961]New Zealand School Property Agency
Drinking water in schools: https://www.schoolproperty.govt.nz/day-to-day-management/water-supply-in-schools/guidance-for-schools-that-supply-their-own-drinking-water
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[bookmark: _Toc240467963]Maintenance and Servicing
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BOIL WATER NOTICE
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All water to be used for drinking and food preparation is to be boiled.
For advice visit Manatū Hauora – Ministry of Health website: 
https://www.health.govt.nz/your-health/healthy-living/drinking-water/water-contamination-events
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