## Slide 1
Water treatment process schematic – roof water supply example
Roof Water Source
School Building 1
Roof Water Source
School Building 2
25 m3
raw water storage tanks x2
25 m3 treated water storage
20 μm
5
μm
Validated UV
Cartridge Filters
SV
FM
Treated water to school buildings and drinking fountains
Flow Meter
Solenoid Valve
= Leaf Screen
= Pressure Gauge
= Pump
= Isolation Valve
= Downpipe Diverter
= First Flush Diverter
= Sample Point

## Slide 2
Water treatment process schematic – roof water supply example
Roof Water Source
School Building 1
Roof Water Source
School Building 2
25 m3
raw water storage tanks x2
25 m3 treated water storage
20 μm
5
μm
Validated UV
Cartridge Filters
SV
FM
Treated water to school buildings and drinking fountains
Flow Meter
Solenoid Valve
= Leaf Screen
= Pressure Gauge
= Pump
= Isolation Valve
= Downpipe Diverter
= First Flush Diverter
= Sample Point
Roof Water Source
School Building 3

## Slide 3
Water treatment process schematic – roof water supply example
Roof Water Source
School Building 1
Roof Water Source
School Building 2
Raw water storage tanks
20 μm
5
μm
UV
Cartridge Filters
Treated water to school buildings and drinking fountains
= Pump
= Isolation Valve
= Sample Point
Roof Water Source
School Building 3

## Slide 4
Existing Bore and Pump
25,000 L PE tank (untreated)
Cartridge Filters
1
μm
= Pump
= Isolation valve
UV
UVI or UV dose Monitor
To school
NRV = Non-return valve
Existing water treatment process schematic – roof and bore water example
20 μm
30,000 L Concrete tank (untreated)
Roof Water Source
(New Block)
Pressure Vessel
FM
= Flow meter
= Closed Isolation valve
Irrigation

## Slide 5
Existing Bore and Pump
Cartridge Filters
1
μm
= Pump
= Isolation valve
UV
UVI or UV dose Monitor
To school
NRV = Non-return valve
Existing water treatment process schematic –bore water example
20 μm
Pressure Vessel
FM
= Flow meter
FM

## Slide 6
Existing Bore and Pump
Cartridge Filters
1
μm
= Pump
= Isolation valve
UV
UVI or UV dose Monitor
To school
NRV = Non-return valve
Existing water treatment process schematic – bore water example
20 μm
Pressure Vessel
FM
= Flow meter
FM
Media Filter
Water sample point
Softener

## Slide 7: Water treatment process schematic – surface water example
20 μm
NRV
1 μm
Cartridge filters
UV
To school and schoolhouse
IV
IV
IV
Chlorine dosing
Water sample point
Water sample point
IV = Isolation valve
NRV = Non-return valve
IV
IV
PE Untreated Tank (30,000 ℓ)
Pump
Pressure tank
8 ℓ
Chlorine chemical container & dosing pump
Surface Water Intake
PE Treated Tank (10,000 ℓ)
NRV
IV
IV