# Increase in electrical demand – Specialised Report requirements

| Who should provide the Specialised Report? | - Certified electrical engineer; or - Licensed electrician; or - A competent person with a similar level of expertise. |
| --- | --- |
| What details should be included in the Specialised Report? | - The existing site chargeable capacity. - The rating of the circuit protection for the site incoming mains conductors i.e. the rating of the distribution pole or pillar fuse. - A detailed electrical single line diagram showing: - The main switchboard, distribution boards and the ratings of their respective main isolators). - The size, types and approximate length of mains and submain cabling (and the number of phases). - Confirmation of how and where any new electrical demand will be connected to the existing installation. |
| Determine if the existing infrastructure will safely meet the increase in load | Can the existing infrastructure safely sustain the increase in demand: - Assess current carrying capacity of existing incoming mains and main switch. - Assess current carrying capacity of the existing and new submains and submain protection. |
| Ensure that any additional electrical demand will not increase voltage drop more than the maximum permissible 5%. | Determine if the new planned electrical installation will result in a voltage drop exceeding 5%, from the site point of supply to the end of any final circuit. |
| If the current infrastructure is not sufficient to safely operate new load, what possible alternative solutions have been explored? | Examples of alternative solutions may include: - Can automated load management be used to ensure that the maximum current carrying capacity is not exceeded and that the maximum permissible 5% volt drop is not exceeded. - Can other technologies be installed to reduce the electrical demand of the existing and the new electrical installation, examples include: - LED lighting. - heat pumps. - Thermal storage (use of appropriate building materials). - Electrical storage (use of battery energy storage systems) - Renewable energy (photovoltaic solar). |